## Release Sources
100 kBPSD Crude & Vacuum Distillation Unit - Hazardous Area Release Source Schedule
CFU-000-EL-HAC-003 Rev A (Issued for review (FEED)), 2026-10-02 ¦ API RP 505 / EI 15 / NFPA 70 Art. 505
Item | Source ID | Source type | Description | Equipment | Fluid | Fluid cat. (EI 15) | Op. T (C) | Op. P (barg) | Grade of release | Ventilation | Zone(s) | Horizontal extent (m) | Vertical extent (EL m) | Gas group | Temp. class | Plan location x / y (m) | Basis | Remarks
1 | RS-001 | Vessel flanges / instruments | C-101 Atmospheric crude fractionator | C-101 | Crude vapours / atm. distillates | B | 134 / 361 | 1.19 / 1.47 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 6.45 | 100.0-147.7 | IIA | T3 | 95.0 / 98.0 | RP 505 vessel / flanged equipment, open area, 3 m
2 | RS-002 | Vessel flanges / instruments | C-102 Kero side stripper | C-102 | Kerosene | C | 220 | 1.26 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3.85 | 100.0-116.6 | IIA | T3 | 106.5 / 98.0 | RP 505 vessel / flanged equipment, open area, 3 m
3 | RS-003 | Vessel flanges / instruments | C-103 Diesel side stripper | C-103 | Diesel | C | 302 | 1.36 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3.95 | 100.0-116.7 | IIA | T3 | 112.5 / 98.0 | RP 505 vessel / flanged equipment, open area, 3 m
4 | RS-004 | Vessel flanges / instruments | C-104 Ago side stripper | C-104 | AGO | C | 343 | 1.44 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3.7 | 100.0-116.5 | IIA | T3 | 118.5 / 98.0 | RP 505 vessel / flanged equipment, open area, 3 m
5 | RS-005 | Vessel flanges / instruments | D-102 Atm. overhead reflux drum (3-phase) | D-102 | Unstabilised naphtha, LPG, sour water (H2S) | A | 45 | 0.7 | Secondary | Open, adequate (natural) | Zone 2, Zone 2 (additional) | Z2: offset 7.5; Z2: R 15 | 100.0-115.9; 100.0-100.6 | IIB | T3 | 79.0 / 90.0 | Pressurised cat. A drum: 7.5 m (EI 15 hazard radius, LPG flange / instrument releases); additional Zone 2 15 m x 0.6 m
6 | RS-006 | Sample point | D-102 boot sour-water / naphtha sample | D-102 | Unstabilised naphtha, LPG, sour water (H2S) | A | 45 | 0.7 | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIB | T3 | 83.0 / 87.3 | Sample point (manual) - EI 15
7 | RS-007 | Exchanger flanges | E-115A Atm. overhead trim condenser | E-115A | Atm. overhead vapour (H2S) | B | H 60->45 / C 32->43 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.1 | IIB | T3 | 79.0 / 95.5 | RP 505 vessel / flanged equipment, open area, 3 m
8 | RS-008 | Exchanger flanges | E-115B Atm. overhead trim condenser | E-115B | Atm. overhead vapour (H2S) | B | H 60->45 / C 32->43 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.1 | IIB | T3 | 79.0 / 98.5 | RP 505 vessel / flanged equipment, open area, 3 m
9 | RS-009 | Vessel flanges / instruments | X-103 Neutraliser / filming amine package (atm OH) | X-103 | Neutralising amine (flammable) | C |  |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.8 | IIA | T3 | 76.0 / 104.0 | RP 505 vessel / flanged equipment, open area, 3 m
10 | RS-010 | Pump seal | P-103A mechanical seal | P-103A | Naphtha reflux | B | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 72.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
11 | RS-011 | Pump seal | P-103B mechanical seal | P-103B | Naphtha reflux | B | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 75.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
12 | RS-012 | Pump seal | P-104A mechanical seal | P-104A | Unstabilised naphtha (C3/C4) | A | 45 |  | Secondary | Open, adequate (natural) | Zone 2, Zone 2 (additional) | Z2: R 7.5; Z2: R 15 | 100.0-107.5; 100.0-100.6 | IIA | T3 | 79.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals; additional Zone 2 15 m x 0.6 m (highly volatile liquid)
13 | RS-013 | Pump seal | P-104B mechanical seal | P-104B | Unstabilised naphtha (C3/C4) | A | 45 |  | Secondary | Open, adequate (natural) | Zone 2, Zone 2 (additional) | Z2: R 7.5; Z2: R 15 | 100.0-107.5; 100.0-100.6 | IIA | T3 | 82.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals; additional Zone 2 15 m x 0.6 m (highly volatile liquid)
14 | RS-014 | Pump seal | P-105A mechanical seal | P-105A | Sour water (H2S, HC traces) | C | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIB | T3 | 85.5 / 83.5 | Low HC content sour water; EI 15 small release
15 | RS-015 | Pump seal | P-105B mechanical seal | P-105B | Sour water (H2S, HC traces) | C | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIB | T3 | 88.5 / 83.5 | Low HC content sour water; EI 15 small release
16 | RS-016 | Pump seal | P-112A mechanical seal | P-112A | Atm. residue > AIT (360 C) | C | 349 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 92.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
17 | RS-017 | Sample point | Atm. residue sample point at P-112A/B discharge | P-112A | Atm. residue > AIT (360 C) | C | 349 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 93.5 / 87.8 | Sample point (manual, intermittent) - EI 15 / RP 505
18 | RS-018 | Pump seal | P-112B mechanical seal | P-112B | Atm. residue > AIT (360 C) | C | 349 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 95.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
19 | RS-019 | Pump seal | P-108A mechanical seal | P-108A | BPA | C | 314 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 98.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
20 | RS-020 | Pump seal | P-108B mechanical seal | P-108B | BPA | C | 314 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 101.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
21 | RS-021 | Pump seal | P-109A mechanical seal | P-109A | Kerosene | C | 212 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 105.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
22 | RS-022 | Sample point | Kerosene product sample point at P-109A/B discharge | P-109A | Kerosene | C | 212 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 106.5 / 86.8 | Sample point (manual, intermittent) - EI 15 / RP 505
23 | RS-023 | Pump seal | P-109B mechanical seal | P-109B | Kerosene | C | 212 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 108.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
24 | RS-024 | Pump seal | P-110A mechanical seal | P-110A | Diesel | C | 294 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 111.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
25 | RS-025 | Sample point | Diesel product sample point at P-110A/B discharge | P-110A | Diesel | C | 294 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 113.0 / 86.8 | Sample point (manual, intermittent) - EI 15 / RP 505
26 | RS-026 | Pump seal | P-110B mechanical seal | P-110B | Diesel | C | 294 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 114.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
27 | RS-027 | Pump seal | P-111A mechanical seal | P-111A | AGO | C | 335 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 118.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
28 | RS-028 | Sample point | AGO product sample point at P-111A/B discharge | P-111A | AGO | C | 335 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 119.5 / 86.8 | Sample point (manual, intermittent) - EI 15 / RP 505
29 | RS-029 | Pump seal | P-111B mechanical seal | P-111B | AGO | C | 335 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 121.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
30 | RS-030 | Pump seal | P-106A mechanical seal | P-106A | TPA (kerosene range) | C | 153 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 124.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
31 | RS-031 | Pump seal | P-106B mechanical seal | P-106B | TPA (kerosene range) | C | 153 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 127.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
32 | RS-032 | Pump seal | P-107A mechanical seal | P-107A | MPA | C | 240 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 131.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
33 | RS-033 | Pump seal | P-107B mechanical seal | P-107B | MPA | C | 240 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 134.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
34 | RS-034 | Vessel flanges / instruments | C-106 Naphtha splitter | C-106 | Light / heavy naphtha | B | 84 / 152 | 1.1 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 4.55 | 100.0-139.3 | IIA | T3 | 52.0 / 100.0 | RP 505 vessel / flanged equipment, open area, 3 m
35 | RS-035 | Vessel flanges / instruments | C-105 Naphtha stabiliser (debutaniser) | C-105 | LPG / naphtha (stabiliser) | A | 79 / 203 | 10.8 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 4.05 | 100.0-125.5 | IIA | T3 | 64.0 / 100.0 | RP 505 vessel / flanged equipment, open area, 3 m
36 | RS-036 | Vessel flanges / instruments | D-106 Splitter reflux drum | D-106 | Light naphtha | B | 50 | 0.8 | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-110.2 | IIA | T3 | 54.0 / 90.5 | RP 505 vessel / flanged equipment, open area, 3 m
37 | RS-037 | Vessel flanges / instruments | D-105 Stabiliser reflux drum | D-105 | LPG | A | 45 | 10.5 | Secondary | Open, adequate (natural) | Zone 2, Zone 2 (additional) | Z2: offset 7.5; Z2: R 15 | 100.0-113.2; 100.0-100.6 | IIA | T3 | 65.5 / 90.5 | Pressurised cat. A drum: 7.5 m (EI 15 hazard radius, LPG flange / instrument releases); additional Zone 2 15 m x 0.6 m
38 | RS-038 | Exchanger flanges | E-117 Splitter reboiler (MP steam) | E-117 | Naphtha | B | H 186->186 / C 144->152 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-110.5 | IIA | T3 | 52.0 / 106.0 | RP 505 vessel / flanged equipment, open area, 3 m
39 | RS-039 | Exchanger flanges | E-116 Stabiliser reboiler (HP steam) | E-116 | Stabiliser bottoms naphtha | B | H 253->253 / C 193->203 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.0 | IIA | T3 | 64.0 / 105.5 | RP 505 vessel / flanged equipment, open area, 3 m
40 | RS-040 | Exchanger flanges | E-114 Stabiliser feed / bottoms | E-114 | Naphtha / LPG | A | H 203->163 / C 45->91 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.0 | IIA | T3 | 70.0 / 100.0 | RP 505 vessel / flanged equipment, open area, 3 m
41 | RS-041 | Pump seal | P-116A mechanical seal | P-116A | Light naphtha | B | 50 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 50.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
42 | RS-042 | Sample point | LN product sample point at P-116A/B discharge | P-116A | Light naphtha | B | 50 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 51.5 / 86.8 | Sample point (manual, intermittent) - EI 15 / RP 505
43 | RS-043 | Pump seal | P-116B mechanical seal | P-116B | Light naphtha | B | 50 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 53.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
44 | RS-044 | Pump seal | P-117A mechanical seal | P-117A | Heavy naphtha | B | 152 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 56.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
45 | RS-045 | Sample point | HN product sample point at P-117A/B discharge | P-117A | Heavy naphtha | B | 152 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 58.0 / 86.8 | Sample point (manual, intermittent) - EI 15 / RP 505
46 | RS-046 | Pump seal | P-117B mechanical seal | P-117B | Heavy naphtha | B | 152 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 59.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
47 | RS-047 | Pump seal | P-115A mechanical seal | P-115A | LPG | A | 45 |  | Secondary | Open, adequate (natural) | Zone 2, Zone 2 (additional) | Z2: R 7.5; Z2: R 15 | 100.0-107.5; 100.0-100.6 | IIA | T3 | 63.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals; additional Zone 2 15 m x 0.6 m (highly volatile liquid)
48 | RS-048 | Sample point | LPG (closed-loop sampler) sample point at P-115A/B discharge | P-115A | LPG | A | 45 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 64.5 / 86.8 | Sample point (manual, intermittent) - EI 15 / RP 505
49 | RS-049 | Pump seal | P-115B mechanical seal | P-115B | LPG | A | 45 |  | Secondary | Open, adequate (natural) | Zone 2, Zone 2 (additional) | Z2: R 7.5; Z2: R 15 | 100.0-107.5; 100.0-100.6 | IIA | T3 | 66.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals; additional Zone 2 15 m x 0.6 m (highly volatile liquid)
50 | RS-050 | Exchanger flanges | E-106A Crude / Middle (kero) pumparound | E-106A | Hydrocarbon (crude / products) | C | H 240->160 / C 136->170 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 12.5 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
51 | RS-051 | Exchanger flanges | E-106B Crude / Middle (kero) pumparound | E-106B | Hydrocarbon (crude / products) | C | H 240->160 / C 136->170 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 16.0 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
52 | RS-052 | Exchanger flanges | E-107 Crude / Diesel product | E-107 | Hydrocarbon (crude / products) | C | H 294->205 / C 170->184 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.0 | IIA | T3 | 19.5 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
53 | RS-053 | Exchanger flanges | E-108A Crude / HVGO pumparound/product | E-108A | Hydrocarbon (crude / products) | C | H 315->205 / C 184->234 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 23.0 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
54 | RS-054 | Exchanger flanges | E-108B Crude / HVGO pumparound/product | E-108B | Hydrocarbon (crude / products) | C | H 315->205 / C 184->234 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 26.5 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
55 | RS-055 | Exchanger flanges | E-108C Crude / HVGO pumparound/product | E-108C | Hydrocarbon (crude / products) | C | H 315->205 / C 184->234 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 30.0 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
56 | RS-056 | Exchanger flanges | E-108D Crude / HVGO pumparound/product | E-108D | Hydrocarbon (crude / products) | C | H 315->205 / C 184->234 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 33.5 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
57 | RS-057 | Exchanger flanges | E-109 Crude / AGO product | E-109 | Hydrocarbon (crude / products) | C | H 335->254 / C 234->241 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.0 | IIA | T3 | 37.0 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
58 | RS-058 | Exchanger flanges | E-110A Crude / Bottom (diesel) pumparound | E-110A | Hydrocarbon (crude / products) | C | H 314->261 / C 241->258 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 40.5 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
59 | RS-059 | Exchanger flanges | E-110B Crude / Bottom (diesel) pumparound | E-110B | Hydrocarbon (crude / products) | C | H 314->261 / C 241->258 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 44.0 / 92.0 | RP 505 vessel / flanged equipment, open area, 3 m
60 | RS-060 | Exchanger flanges | E-111A Crude / Vacuum residue | E-111A | Hydrocarbon (crude / products) | C | H 366->278 / C 258->274 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 12.5 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
61 | RS-061 | Exchanger flanges | E-111B Crude / Vacuum residue | E-111B | Hydrocarbon (crude / products) | C | H 366->278 / C 258->274 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 16.0 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
62 | RS-062 | Exchanger flanges | E-101 Crude / Top pumparound | E-101 | Hydrocarbon (crude / products) | C | H 153->83 / C 30->56 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.0 | IIA | T3 | 19.5 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
63 | RS-063 | Exchanger flanges | E-102 Crude / Kerosene product | E-102 | Hydrocarbon (crude / products) | C | H 212->76 / C 56->75 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 23.0 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
64 | RS-064 | Exchanger flanges | E-103A Crude / LVGO pumparound/product | E-103A | Hydrocarbon (crude / products) | C | H 224->95 / C 75->108 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 26.5 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
65 | RS-065 | Exchanger flanges | E-103B Crude / LVGO pumparound/product | E-103B | Hydrocarbon (crude / products) | C | H 224->95 / C 75->108 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 30.0 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
66 | RS-066 | Exchanger flanges | E-104 Crude / Diesel product | E-104 | Hydrocarbon (crude / products) | C | H 205->128 / C 108->121 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.0 | IIA | T3 | 33.5 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
67 | RS-067 | Exchanger flanges | E-105 Crude / Vacuum residue | E-105 | Hydrocarbon (crude / products) | C | H 255->175 / C 121->136 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.2 | IIA | T3 | 37.0 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
68 | RS-068 | Exchanger flanges | E-113 BPA / MP steam generator (kettle) | E-113 | Hydrocarbon (crude / products) | C | H 261->224 / C 186->186 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.0 | IIA | T3 | 40.5 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
69 | RS-069 | Exchanger flanges | E-201 VR / LP steam generator (kettle) | E-201 | Hydrocarbon (crude / products) | C | H 278->255 / C 148->148 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.0 | IIA | T3 | 44.0 / 109.0 | RP 505 vessel / flanged equipment, open area, 3 m
70 | RS-070 | Pump seal | P-101A mechanical seal | P-101A | Crude (with light ends) | B | 30 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 14.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
71 | RS-071 | Sample point | Crude sample point at P-101A/B discharge | P-101A | Crude (with light ends) | B | 30 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 15.5 / 87.8 | Sample point (manual, intermittent) - EI 15 / RP 505
72 | RS-072 | Pump seal | P-101B mechanical seal | P-101B | Crude (with light ends) | B | 30 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 18.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
73 | RS-073 | Vessel flanges / instruments | D-104 Flare knock-out drum (unit) | D-104 | Flare KO liquids / gas | G | 60 | 0.2 | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.7 | IIB | T3 | 135.0 / 128.0 | RP 505 vessel / flanged equipment, open area, 3 m
74 | RS-074 | Vessel flanges / instruments | D-101A Electrostatic desalter, 1st stage | D-101A | Crude + wash water, 136 C, 11.5 barg | B | 136 | 11.5 | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-108.3 | IIA | T3 | 36.0 / 52.0 | RP 505 vessel / flanged equipment, open area, 3 m
75 | RS-075 | Sample point | D-101A interface try-cocks / profiler sample | D-101A | Crude + wash water, 136 C, 11.5 barg | B | 136 | 11.5 | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.5; 100.0-104.0 | IIA | T3 | 19.1 / 52.0 | Sample point (manual) - EI 15
76 | RS-076 | Vessel flanges / instruments | D-101B Electrostatic desalter, 2nd stage | D-101B | Crude + wash water, 136 C, 11.5 barg | B | 136 | 11.5 | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-108.3 | IIA | T3 | 36.0 / 42.0 | RP 505 vessel / flanged equipment, open area, 3 m
77 | RS-077 | Sample point | D-101B interface try-cocks / profiler sample | D-101B | Crude + wash water, 136 C, 11.5 barg | B | 136 | 11.5 | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.5; 100.0-104.0 | IIA | T3 | 19.1 / 42.0 | Sample point (manual) - EI 15
78 | RS-078 | Vessel flanges / instruments | X-101 Demulsifier injection package | X-101 | Demulsifier (aromatic solvent) | C |  |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.8 | IIA | T3 | 58.0 / 55.0 | RP 505 vessel / flanged equipment, open area, 3 m
79 | RS-079 | Pump seal | P-102A mechanical seal | P-102A | Desalted crude, 135 C | B | 136 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 46.0 / 65.5 | RP 505 pump figure (HTA, open area); API 682 seals
80 | RS-080 | Pump seal | P-102B mechanical seal | P-102B | Desalted crude, 135 C | B | 136 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 50.5 / 65.5 | RP 505 pump figure (HTA, open area); API 682 seals
81 | RS-081 | Vessel flanges / instruments | D-103 Fuel gas knock-out drum | D-103 | Refinery fuel gas (H2 < 30 vol% assumed) | G | 30 | 3.5 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3.45 | 100.0-107.2 | IIB | T3 | 146.0 / 22.0 | RP 505 vessel / flanged equipment, open area, 3 m
82 | RS-082 | Vessel flanges / instruments | C-201 Vacuum column (wet, packed) | C-201 | Vacuum gas oils / residue (sub-atmospheric) | C | 70 / 386 | 20 / 60 mbar(a) | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 6.3 | 100.0-150.1 | IIA | T3 | 175.0 / 98.0 | RP 505 vessel / flanged equipment, open area, 3 m
83 | RS-085 | Ejector / condenser flanges | J-201..203 / E-202..204 (ST-201) 1st-stage ejector intercondenser | J-201..203 / E-202..204 (ST-201) | Ejector condensers: steam, HC, H2S | G |  |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-127.0 | IIB | T3 | 196.0 / 97.5 | Flanged ejector set on structure, 3 m around structure
84 | RS-086 | Vessel flanges / instruments | D-201 Ejector hotwell / sour water separator | D-201 | Hotwell: sour water, slop oil, NCG with H2S | G | 45 | 0.05 | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-104.9 | IIB | T3 | 196.0 / 106.0 | RP 505 vessel / flanged equipment, open area, 3 m
85 | RS-087 | Atmospheric vent | D-201 hotwell seal-leg / atmospheric vent outlet | D-201 | Hotwell: sour water, slop oil, NCG with H2S | G | 45 | 0.05 | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1.5; Z2: R 4.5 | 103.4-106.4; 100.0-109.4 | IIB | T3 | 198.0 / 106.0 | RP 505 atmospheric vent: Zone 1 1.5 m, Zone 2 4.5 m to grade (HTA) | Vent outlet 3 m above drum top; route to H-201 off-gas system preferred (HAZOP)
86 | RS-088 | Vessel flanges / instruments | D-202 Vacuum off-gas knock-out drum | D-202 | Vacuum off-gas (H2S) | G | 45 | 0.05 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3.3 | 100.0-106.6 | IIB | T3 | 203.0 / 106.0 | RP 505 vessel / flanged equipment, open area, 3 m
87 | RS-089 | Vessel flanges / instruments | X-104 Corrosion inhibitor package (VDU OH) | X-104 | Corrosion inhibitor (solvent) | C |  |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 100.0-105.8 | IIA | T3 | 209.0 / 106.0 | RP 505 vessel / flanged equipment, open area, 3 m
88 | RS-090 | Pump seal | P-204A mechanical seal | P-204A | Vacuum residue > AIT | C | 366 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 172.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
89 | RS-091 | Sample point | VR product sample point at P-204A/B discharge | P-204A | Vacuum residue > AIT | C | 366 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 173.5 / 86.8 | Sample point (manual, intermittent) - EI 15 / RP 505
90 | RS-092 | Pump seal | P-204B mechanical seal | P-204B | Vacuum residue > AIT | C | 366 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 175.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
91 | RS-093 | Pump seal | P-203A mechanical seal | P-203A | Slop wax | C | 378 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 178.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
92 | RS-094 | Pump seal | P-203B mechanical seal | P-203B | Slop wax | C | 378 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 181.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
93 | RS-095 | Pump seal | P-202A mechanical seal | P-202A | HVGO | C | 315 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 185.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
94 | RS-096 | Sample point | HVGO product sample point at P-202A/B discharge | P-202A | HVGO | C | 315 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 186.5 / 86.8 | Sample point (manual, intermittent) - EI 15 / RP 505
95 | RS-097 | Pump seal | P-202B mechanical seal | P-202B | HVGO | C | 315 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 188.0 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
96 | RS-098 | Pump seal | P-201A mechanical seal | P-201A | LVGO | C | 224 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 191.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
97 | RS-099 | Sample point | LVGO product sample point at P-201A/B discharge | P-201A | LVGO | C | 224 |  | Primary | Open, adequate (natural) | Zone 1, Zone 2 | Z1: R 1; Z2: R 3 | 100.0-102.0; 100.0-104.0 | IIA | T3 | 193.0 / 86.8 | Sample point (manual, intermittent) - EI 15 / RP 505
98 | RS-100 | Pump seal | P-201B mechanical seal | P-201B | LVGO | C | 224 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIA | T3 | 194.5 / 83.5 | RP 505 pump figure (HTA, open area); API 682 seals
99 | RS-101 | Pump seal | P-205A mechanical seal | P-205A | Hotwell sour water | C | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIB | T3 | 193.0 / 111.5 | Low HC content sour water; EI 15 small release
100 | RS-102 | Pump seal | P-205B mechanical seal | P-205B | Hotwell sour water | C | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIB | T3 | 196.0 / 111.5 | Low HC content sour water; EI 15 small release
101 | RS-103 | Pump seal | P-206A mechanical seal | P-206A | Hotwell slop oil | C | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIB | T3 | 199.5 / 111.5 | RP 505 pump figure (HTA, open area); API 682 seals
102 | RS-104 | Pump seal | P-206B mechanical seal | P-206B | Hotwell slop oil | C | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 7.5 | 100.0-107.5 | IIB | T3 | 202.5 / 111.5 | RP 505 pump figure (HTA, open area); API 682 seals
103 | RS-105 | Header box plugs / flanges | A-107-B1 headers on rack structure | A-107 | Light naphtha | B | 84->50 (air 35->45) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIA | T3 | 51.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
104 | RS-106 | Header box plugs / flanges | A-107-B2 headers on rack structure | A-107 | Light naphtha | B | 84->50 (air 35->45) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIA | T3 | 57.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
105 | RS-107 | Header box plugs / flanges | A-106 headers on rack structure | A-106 | LPG / stabiliser OH | A | 79->45 (air 35->40) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIA | T3 | 57.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
106 | RS-108 | Header box plugs / flanges | A-108 headers on rack structure | A-108 | Heavy naphtha | B | 152->45 (air 35->40) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIA | T3 | 63.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
107 | RS-109 | Header box plugs / flanges | A-101-B1 headers on rack structure | A-101 | Atm. overhead vapour / naphtha (H2S) | B | 134->60 (air 35->55) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIB | T3 | 75.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
108 | RS-110 | Header box plugs / flanges | A-101-B2 headers on rack structure | A-101 | Atm. overhead vapour / naphtha (H2S) | B | 134->60 (air 35->55) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIB | T3 | 81.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
109 | RS-111 | Header box plugs / flanges | A-101-B3 headers on rack structure | A-101 | Atm. overhead vapour / naphtha (H2S) | B | 134->60 (air 35->55) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIB | T3 | 87.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
110 | RS-112 | Header box plugs / flanges | A-103 headers on rack structure | A-103 | Kerosene | C | 76->45 (air 35->40) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIA | T3 | 111.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
111 | RS-113 | Header box plugs / flanges | A-104 headers on rack structure | A-104 | Diesel | C | 128->55 (air 35->50) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIA | T3 | 117.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
112 | RS-114 | Header box plugs / flanges | A-105 headers on rack structure | A-105 | AGO | C | 254->60 (air 35->55) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIA | T3 | 123.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
113 | RS-115 | Header box plugs / flanges | A-201 headers on rack structure | A-201 | LVGO | C | 95->55 (air 35->50) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIA | T3 | 159.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
114 | RS-116 | Header box plugs / flanges | A-202 headers on rack structure | A-202 | HVGO | C | 205->90 (air 35->60) |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: offset 3 | 112.0-120.5 | IIA | T3 | 165.0 / 75.0 | RP 505 elevated flanged equipment, 3 m around (no grade extension: covered by rack/pump sources)
115 | RS-117 | Control-valve station | Control valves FV-1031 (C-101) | C-101 | Crude vapours / atm. distillates | B | 134 / 361 | 1.19 / 1.47 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 95.0 / 92.5 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
116 | RS-118 | Control-valve station | Control valves FV-1050 (C-102) | C-102 | Kerosene | C | 220 | 1.26 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 106.5 / 95.2 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
117 | RS-119 | Control-valve station | Control valves FV-1060 (C-103) | C-103 | Diesel | C | 302 | 1.36 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 112.5 / 95.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
118 | RS-120 | Control-valve station | Control valves FV-1070 (C-104) | C-104 | AGO | C | 343 | 1.44 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 118.5 / 95.3 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
119 | RS-121 | Control-valve station | Control valves FV-1034, FV-1094, LV-1097, PV-1091 (C-105) | C-105 | LPG / naphtha (stabiliser) | A | 79 / 203 | 10.8 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 64.0 / 97.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
120 | RS-122 | Control-valve station | Control valves FV-1103, PV-1100 (C-106) | C-106 | Light / heavy naphtha | B | 84 / 152 | 1.1 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 52.0 / 96.5 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
121 | RS-123 | Control-valve station | Control valves PV-2010 (C-201) | C-201 | Vacuum gas oils / residue (sub-atmospheric) | C | 70 / 386 | 20 / 60 mbar(a) | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 175.0 / 92.7 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
122 | RS-124 | Control-valve station | Control valves LV-1008, PDV-1005, PDV-1006, PV-1009, TV-1004 (D-101) | D-101 | Crude + wash water, 136 C, 11.5 barg | B |  |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 36.0 / 55.9 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
123 | RS-125 | Control-valve station | Control valves LV-1035, PV-1032A, PV-1032B (D-102) | D-102 | Unstabilised naphtha, LPG, sour water (H2S) | A | 45 | 0.7 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIB | T3 | 79.0 / 86.3 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
124 | RS-126 | Control-valve station | Control valves LV-9002 (D-103) | D-103 | Refinery fuel gas (H2 < 30 vol% assumed) | G | 30 | 3.5 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIB | T3 | 146.0 / 24.4 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
125 | RS-127 | Control-valve station | Control valves LV-2028, LV-2029 (D-201) | D-201 | Hotwell: sour water, slop oil, NCG with H2S | G | 45 | 0.05 | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIB | T3 | 196.0 / 103.3 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
126 | RS-128 | Control-valve station | Control valves TV-1041 (E-101) | E-101 | Hydrocarbon (crude / products) | C | H 153->83 / C 30->56 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 19.5 / 103.2 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
127 | RS-129 | Control-valve station | Control valves TV-1043 (E-106) | E-106 | Hydrocarbon (crude / products) | C | H 240->160 / C 136->170 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 12.5 / 86.2 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
128 | RS-130 | Control-valve station | Control valves TV-2017 (E-108) | E-108 | Hydrocarbon (crude / products) | C | H 315->205 / C 184->234 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 23.0 / 86.2 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
129 | RS-131 | Control-valve station | Control valves TV-1045 (E-113) | E-113 | Hydrocarbon (crude / products) | C | H 261->224 / C 186->186 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 40.5 / 103.8 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
130 | RS-132 | Control-valve station | Control valves FV-1011, FV-1012, FV-1013, FV-1014, FV-1015, FV-1016, FV-1017, FV-1018 (H-101) | H-101 | Heater charge (crude / atm. residue) | C | 274 -> 366 | 2.37 outlet | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 98.0 / 62.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
131 | RS-133 | Control-valve station | Control valves FV-1083, FV-2001, FV-2002, FV-2003, FV-2004, PV-2031 (H-201) | H-201 | Heater charge (crude / atm. residue) | C | 349 -> 398 | -0.70 outlet | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 172.0 / 62.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
132 | RS-134 | Control-valve station | Control valves FV-1001 (P-101) | P-101 | Crude (with light ends) | B | 30 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 15.5 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
133 | RS-135 | Control-valve station | Control valves FV-1034 (P-104) | P-104 | Unstabilised naphtha (C3/C4) | A | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 80.5 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
134 | RS-136 | Control-valve station | Control valves FV-1040 (P-106) | P-106 | TPA (kerosene range) | C | 153 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 126.0 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
135 | RS-137 | Control-valve station | Control valves FV-1042 (P-107) | P-107 | MPA | C | 240 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 132.5 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
136 | RS-138 | Control-valve station | Control valves FV-1044 (P-108) | P-108 | BPA | C | 314 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 100.0 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
137 | RS-139 | Control-valve station | Control valves FV-1052 (P-109) | P-109 | Kerosene | C | 212 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 106.5 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
138 | RS-140 | Control-valve station | Control valves FV-1062 (P-110) | P-110 | Diesel | C | 294 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 113.0 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
139 | RS-141 | Control-valve station | Control valves FV-1072 (P-111) | P-111 | AGO | C | 335 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 119.5 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
140 | RS-142 | Control-valve station | Control valves FV-1093 (P-115) | P-115 | LPG | A | 45 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 64.5 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
141 | RS-143 | Control-valve station | Control valves FV-1102 (P-116) | P-116 | Light naphtha | B | 50 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 51.5 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
142 | RS-144 | Control-valve station | Control valves FV-1107 (P-117) | P-117 | Heavy naphtha | B | 152 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 58.0 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
143 | RS-145 | Control-valve station | Control valves FV-2011, FV-2015 (P-201) | P-201 | LVGO | C | 224 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 193.0 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
144 | RS-146 | Control-valve station | Control valves FV-2016, FV-2019 (P-202) | P-202 | HVGO | C | 315 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 186.5 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
145 | RS-147 | Control-valve station | Control valves FV-2022 (P-203) | P-203 | Slop wax | C | 378 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 180.0 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)
146 | RS-148 | Control-valve station | Control valves FV-2025 (P-204) | P-204 | Vacuum residue > AIT | C | 366 |  | Secondary | Open, adequate (natural) | Zone 2 | Z2: R 3 | 100.0-104.0 | IIA | T3 | 173.5 / 88.0 | RP 505 valve stations (stem packing, flanges), 3 m | Indicative location (P&ID / piping layout not yet issued)

## Unclassified items
Item | Status | Clearance to nearest Zone 2 (m) | Nearest source | Description
H-101 | Fired heater - ignition source; not classified (RP 505 fired-equipment practice) | 10.3 | RS-132 | Control valves FV-1011, FV-1012, FV-1013, FV-1014, FV-1015, FV-1016, FV-1017, FV-1018 (H-101)
H-201 | Fired heater - ignition source; not classified | 13.2 | RS-126 | Control valves LV-9002 (D-103)
E-120 | Air preheater (air / flue gas only) | 34.1 | RS-132 | Control valves FV-1011, FV-1012, FV-1013, FV-1014, FV-1015, FV-1016, FV-1017, FV-1018 (H-101)
SS-100 | Substation - non-classified, pressurised | 17.1 | RS-076 | D-101B Electrostatic desalter, 2nd stage
FAR-100 | Field auxiliary room - non-classified, pressurised | 20.1 | RS-076 | D-101B Electrostatic desalter, 2nd stage

## Fluid categories
A | Cat. A - flammable liquid which on release vaporises rapidly and substantially (LPG, unstabilised naphtha)
B | Cat. B - flammable liquid at a temperature sufficient for boiling on release (crude, naphtha)
C | Cat. C - flammable liquid that may be above its flash point or form a mist on release (kerosene, diesel, gas oils, residue)
G | Cat. G(i) - refinery fuel gas / off-gas (may contain H2, H2S)
N | Non-flammable (water, brine, caustic, steam) - not a release source

## Equipment protection
Equipment | Zone 1 | Zone 2
LV motors (480 V) | Ex db or Ex eb (tE, stall relay), IIB T3 (Gb) | Ex ec (non-sparking), IIA/IIB T3 (Gc); AEx ec per NEC 505
MV motors (4.16 kV) | Not located in Zone 1 (relocate) / Ex pxb | Ex ec with stator discharge risk assessment / pre-start purge, IIA T3
VFD-fed motors | Ex db certified with the drive (converter duty) | Ex ec certified for converter duty; T-class verified with VFD
Instruments | Ex ia / ib (intrinsic safety), Ex db | Ex ia / ic, Ex db, Ex ec
Lighting fittings | Ex db / eb, IIB T3 | Ex ec / nR, IIA T3 (IIB in H2S areas)
Junction boxes / glands | Ex eb boxes; Ex db barrier glands for Ex d | Ex eb / ec boxes and glands
Heat tracing | Ex 60079-30-1, stabilised design <= T3 | Ex 60079-30-1, self-regulating, T3
Desalter transformers | n/a (Zone 2 only) | Vendor package certified for Zone 2 (Ex o / ec), HV entry to vessel via Ex bushings
Welding / receptacles | Not permitted | Ex de interlocked receptacles; hot-work permit
Buildings SS-100 / FAR-100 | - | Non-classified; pressurised (NFPA 496 / IEC 60079-13), intakes in unclassified area, gas detection