## Load List
100 kBPSD Crude & Vacuum Distillation Unit - Electrical Load List
CFU-000-EL-LDL-001 Rev A (Issued for review (FEED)), 2026-10-02 ¦ Generic Refinery - Gulf Coast
Item | Tag | Description | Equip. | Category | Volt (V) | Starter / feeder | Bus | Rated kW | Rated kVA | Absorbed kW | Load factor | Eff. | PF | Input kW | kvar | kVA | Duty | C kW | I kW | S kW | C kvar | I kvar | S kvar | Notes
1 | P-101A | Crude charge pump A | P-101A/B | Pumps | 4160 | VCB-DOL | SWG-102A | 710 |  | 616.68 | 0.87 | 0.965 | 0.89 | 639.05 | 327.4 | 718.04 | Continuous | 639.05 | 0 | 0 | 327.4 | 0 | 0
2 | P-101B | Crude charge pump B | P-101A/B | Pumps | 4160 | VCB-DOL | SWG-102B | 710 |  | 616.68 | 0.87 | 0.965 | 0.89 | 639.05 | 327.4 | 718.04 | Standby | 0 | 0 | 639.05 | 0 | 0 | 327.4
3 | P-102A | Desalted crude booster pump A | P-102A/B | Pumps | 4160 | VCB-DOL | SWG-102A | 710 |  | 615.86 | 0.87 | 0.965 | 0.89 | 638.2 | 326.96 | 717.07 | Standby | 0 | 0 | 638.2 | 0 | 0 | 326.96
4 | P-102B | Desalted crude booster pump B | P-102A/B | Pumps | 4160 | VCB-DOL | SWG-102B | 710 |  | 615.86 | 0.87 | 0.965 | 0.89 | 638.2 | 326.96 | 717.07 | Continuous | 638.2 | 0 | 0 | 326.96 | 0 | 0
5 | P-112A | Atm. residue / vacuum heater charge pump A | P-112A/B | Pumps | 4160 | VCB-DOL | SWG-102A | 315 |  | 267.54 | 0.85 | 0.955 | 0.87 | 280.15 | 158.77 | 322.01 | Standby | 0 | 0 | 280.15 | 0 | 0 | 158.77
6 | P-112B | Atm. residue / vacuum heater charge pump B | P-112A/B | Pumps | 4160 | VCB-DOL | SWG-102B | 315 |  | 267.54 | 0.85 | 0.955 | 0.87 | 280.15 | 158.77 | 322.01 | Continuous | 280.15 | 0 | 0 | 158.77 | 0 | 0
7 | P-202A | HVGO pumparound / product pump A | P-202A/B | Pumps | 4160 | VCB-DOL | SWG-102A | 200 |  | 154.82 | 0.77 | 0.955 | 0.87 | 162.12 | 91.88 | 186.34 | Continuous | 162.12 | 0 | 0 | 91.88 | 0 | 0
8 | P-202B | HVGO pumparound / product pump B | P-202A/B | Pumps | 4160 | VCB-DOL | SWG-102B | 200 |  | 154.82 | 0.77 | 0.955 | 0.87 | 162.12 | 91.88 | 186.34 | Standby | 0 | 0 | 162.12 | 0 | 0 | 91.88
9 | K-102A | H-101 induced-draft fan A | K-102A/B | Fired-heater fans | 4160 | VFD | SWG-102A | 200 |  | 170.11 | 0.85 | 0.955 | 0.95 | 183.64 | 60.36 | 193.3 | Continuous | 183.64 | 0 | 0 | 60.36 | 0 | 0
10 | K-102B | H-101 induced-draft fan B | K-102A/B | Fired-heater fans | 4160 | VFD | SWG-102B | 200 |  | 170.11 | 0.85 | 0.955 | 0.95 | 183.64 | 60.36 | 193.3 | Standby | 0 | 0 | 183.64 | 0 | 0 | 60.36
11 | P-103A | Atm. reflux pump A | P-103A/B | Pumps | 480 | DOL | MCC-101A | 55 |  | 46.03 | 0.84 | 0.935 | 0.86 | 49.23 | 29.21 | 57.24 | Standby | 0 | 0 | 49.23 | 0 | 0 | 29.21
12 | P-103B | Atm. reflux pump B | P-103A/B | Pumps | 480 | DOL | MCC-101B | 55 |  | 46.03 | 0.84 | 0.935 | 0.86 | 49.23 | 29.21 | 57.24 | Continuous | 49.23 | 0 | 0 | 29.21 | 0 | 0
13 | P-104A | Unstabilised naphtha pump A | P-104A/B | Pumps | 480 | DOL | MCC-101A | 160 |  | 118.56 | 0.74 | 0.95 | 0.87 | 124.8 | 70.73 | 143.45 | Continuous | 124.8 | 0 | 0 | 70.73 | 0 | 0
14 | P-104B | Unstabilised naphtha pump B | P-104A/B | Pumps | 480 | DOL | MCC-101B | 160 |  | 118.56 | 0.74 | 0.95 | 0.87 | 124.8 | 70.73 | 143.45 | Standby | 0 | 0 | 124.8 | 0 | 0 | 70.73
15 | P-105A | Overhead sour water pump A | P-105A/B | Pumps | 480 | DOL | MCC-101A | 5.5 |  | 3.42 | 0.62 | 0.875 | 0.82 | 3.91 | 2.73 | 4.77 | Standby | 0 | 0 | 3.91 | 0 | 0 | 2.73
16 | P-105B | Overhead sour water pump B | P-105A/B | Pumps | 480 | DOL | MCC-101B | 5.5 |  | 3.42 | 0.62 | 0.875 | 0.82 | 3.91 | 2.73 | 4.77 | Continuous | 3.91 | 0 | 0 | 2.73 | 0 | 0
17 | P-106A | TPA pumparound pump A | P-106A/B | Pumps | 480 | DOL | MCC-101A | 110 |  | 94.04 | 0.85 | 0.95 | 0.87 | 98.99 | 56.1 | 113.78 | Standby | 0 | 0 | 98.99 | 0 | 0 | 56.1
18 | P-106B | TPA pumparound pump B | P-106A/B | Pumps | 480 | DOL | MCC-101B | 110 |  | 94.04 | 0.85 | 0.95 | 0.87 | 98.99 | 56.1 | 113.78 | Continuous | 98.99 | 0 | 0 | 56.1 | 0 | 0
19 | P-107A | MPA pumparound pump A | P-107A/B | Pumps | 480 | DOL | MCC-101A | 160 |  | 122.78 | 0.77 | 0.95 | 0.87 | 129.24 | 73.24 | 148.55 | Standby | 0 | 0 | 129.24 | 0 | 0 | 73.24
20 | P-107B | MPA pumparound pump B | P-107A/B | Pumps | 480 | DOL | MCC-101B | 160 |  | 122.78 | 0.77 | 0.95 | 0.87 | 129.24 | 73.24 | 148.55 | Continuous | 129.24 | 0 | 0 | 73.24 | 0 | 0
21 | P-108A | BPA pumparound pump A | P-108A/B | Pumps | 480 | DOL | MCC-101A | 132 |  | 101.75 | 0.77 | 0.95 | 0.87 | 107.11 | 60.7 | 123.11 | Continuous | 107.11 | 0 | 0 | 60.7 | 0 | 0
22 | P-108B | BPA pumparound pump B | P-108A/B | Pumps | 480 | DOL | MCC-101B | 132 |  | 101.75 | 0.77 | 0.95 | 0.87 | 107.11 | 60.7 | 123.11 | Standby | 0 | 0 | 107.11 | 0 | 0 | 60.7
23 | P-109A | Kero product pump A | P-109A/B | Pumps | 480 | DOL | MCC-101A | 55 |  | 45.98 | 0.84 | 0.935 | 0.86 | 49.17 | 29.18 | 57.18 | Continuous | 49.17 | 0 | 0 | 29.18 | 0 | 0
24 | P-109B | Kero product pump B | P-109A/B | Pumps | 480 | DOL | MCC-101B | 55 |  | 45.98 | 0.84 | 0.935 | 0.86 | 49.17 | 29.18 | 57.18 | Standby | 0 | 0 | 49.17 | 0 | 0 | 29.18
25 | P-110A | Diesel product pump A | P-110A/B | Pumps | 480 | DOL | MCC-101A | 75 |  | 56.49 | 0.75 | 0.935 | 0.86 | 60.42 | 35.85 | 70.25 | Continuous | 60.42 | 0 | 0 | 35.85 | 0 | 0
26 | P-110B | Diesel product pump B | P-110A/B | Pumps | 480 | DOL | MCC-101B | 75 |  | 56.49 | 0.75 | 0.935 | 0.86 | 60.42 | 35.85 | 70.25 | Standby | 0 | 0 | 60.42 | 0 | 0 | 35.85
27 | P-111A | Ago product pump A | P-111A/B | Pumps | 480 | DOL | MCC-101A | 45 |  | 32.35 | 0.72 | 0.935 | 0.86 | 34.6 | 20.53 | 40.23 | Continuous | 34.6 | 0 | 0 | 20.53 | 0 | 0
28 | P-111B | Ago product pump B | P-111A/B | Pumps | 480 | DOL | MCC-101B | 45 |  | 32.35 | 0.72 | 0.935 | 0.86 | 34.6 | 20.53 | 40.23 | Standby | 0 | 0 | 34.6 | 0 | 0 | 20.53
29 | P-114A | Desalter wash water pump A | P-114A/B | Pumps | 480 | DOL | MCC-101A | 30 |  | 23.09 | 0.77 | 0.91 | 0.85 | 25.37 | 15.72 | 29.85 | Standby | 0 | 0 | 25.37 | 0 | 0 | 15.72
30 | P-114B | Desalter wash water pump B | P-114A/B | Pumps | 480 | DOL | MCC-101B | 30 |  | 23.09 | 0.77 | 0.91 | 0.85 | 25.37 | 15.72 | 29.85 | Continuous | 25.37 | 0 | 0 | 15.72 | 0 | 0
31 | P-115A | Stabiliser reflux / LPG pump A | P-115A/B | Pumps | 480 | DOL | MCC-101A | 18.5 |  | 13.88 | 0.75 | 0.91 | 0.85 | 15.26 | 9.45 | 17.95 | Standby | 0 | 0 | 15.26 | 0 | 0 | 9.45
32 | P-115B | Stabiliser reflux / LPG pump B | P-115A/B | Pumps | 480 | DOL | MCC-101B | 18.5 |  | 13.88 | 0.75 | 0.91 | 0.85 | 15.26 | 9.45 | 17.95 | Continuous | 15.26 | 0 | 0 | 9.45 | 0 | 0
33 | P-116A | Splitter reflux / LN pump A | P-116A/B | Pumps | 480 | DOL | MCC-101A | 55 |  | 42.62 | 0.77 | 0.935 | 0.86 | 45.59 | 27.05 | 53.01 | Standby | 0 | 0 | 45.59 | 0 | 0 | 27.05
34 | P-116B | Splitter reflux / LN pump B | P-116A/B | Pumps | 480 | DOL | MCC-101B | 55 |  | 42.62 | 0.77 | 0.935 | 0.86 | 45.59 | 27.05 | 53.01 | Continuous | 45.59 | 0 | 0 | 27.05 | 0 | 0
35 | P-117A | Heavy naphtha product pump A | P-117A/B | Pumps | 480 | DOL | MCC-101A | 45 |  | 35.63 | 0.79 | 0.935 | 0.86 | 38.11 | 22.61 | 44.31 | Continuous | 38.11 | 0 | 0 | 22.61 | 0 | 0
36 | P-117B | Heavy naphtha product pump B | P-117A/B | Pumps | 480 | DOL | MCC-101B | 45 |  | 35.63 | 0.79 | 0.935 | 0.86 | 38.11 | 22.61 | 44.31 | Standby | 0 | 0 | 38.11 | 0 | 0 | 22.61
37 | P-118 | Desalter mud-wash / recycle (single, intermittent) | P-118 | Pumps | 480 | DOL | MCC-101B | 7.5 |  | 5.35 | 0.71 | 0.875 | 0.82 | 6.12 | 4.27 | 7.46 | Intermittent | 0 | 6.12 | 0 | 0 | 4.27 | 0
38 | P-119A | Flare KO drum pump-out pump A | P-119A/B | Pumps | 480 | DOL | MCC-101A | 7.5 |  | 5.74 | 0.76 | 0.875 | 0.82 | 6.56 | 4.58 | 8 | Continuous | 6.56 | 0 | 0 | 4.58 | 0 | 0
39 | P-119B | Flare KO drum pump-out pump B | P-119A/B | Pumps | 480 | DOL | MCC-101B | 7.5 |  | 5.74 | 0.76 | 0.875 | 0.82 | 6.56 | 4.58 | 8 | Standby | 0 | 0 | 6.56 | 0 | 0 | 4.58
40 | P-201A | LVGO pumparound / product pump A | P-201A/B | Pumps | 480 | DOL | MCC-101A | 110 |  | 81.26 | 0.74 | 0.95 | 0.87 | 85.54 | 48.48 | 98.32 | Continuous | 85.54 | 0 | 0 | 48.48 | 0 | 0
41 | P-201B | LVGO pumparound / product pump B | P-201A/B | Pumps | 480 | DOL | MCC-101B | 110 |  | 81.26 | 0.74 | 0.95 | 0.87 | 85.54 | 48.48 | 98.32 | Standby | 0 | 0 | 85.54 | 0 | 0 | 48.48
42 | P-203A | Slop wax pump A | P-203A/B | Pumps | 480 | DOL | MCC-101A | 5.5 |  | 4.65 | 0.85 | 0.875 | 0.82 | 5.32 | 3.71 | 6.48 | Continuous | 5.32 | 0 | 0 | 3.71 | 0 | 0
43 | P-203B | Slop wax pump B | P-203A/B | Pumps | 480 | DOL | MCC-101B | 5.5 |  | 4.65 | 0.85 | 0.875 | 0.82 | 5.32 | 3.71 | 6.48 | Standby | 0 | 0 | 5.32 | 0 | 0 | 3.71
44 | P-204A | Vacuum residue (incl. quench) pump A | P-204A/B | Pumps | 480 | DOL | MCC-101A | 132 |  | 112.28 | 0.85 | 0.95 | 0.87 | 118.18 | 66.98 | 135.84 | Standby | 0 | 0 | 118.18 | 0 | 0 | 66.98
45 | P-204B | Vacuum residue (incl. quench) pump B | P-204A/B | Pumps | 480 | DOL | MCC-101B | 132 |  | 112.28 | 0.85 | 0.95 | 0.87 | 118.18 | 66.98 | 135.84 | Continuous | 118.18 | 0 | 0 | 66.98 | 0 | 0
46 | P-205A | Hotwell sour water pump A | P-205A/B | Pumps | 480 | DOL | MCC-101A | 3.7 |  | 3.21 | 0.87 | 0.875 | 0.82 | 3.66 | 2.56 | 4.47 | Continuous | 3.66 | 0 | 0 | 2.56 | 0 | 0
47 | P-205B | Hotwell sour water pump B | P-205A/B | Pumps | 480 | DOL | MCC-101B | 3.7 |  | 3.21 | 0.87 | 0.875 | 0.82 | 3.66 | 2.56 | 4.47 | Standby | 0 | 0 | 3.66 | 0 | 0 | 2.56
48 | P-206A | Hotwell slop oil pump A | P-206A/B | Pumps | 480 | DOL | MCC-101A | 0.75 |  | 0.16 | 0.22 | 0.8 | 0.76 | 0.2 | 0.17 | 0.27 | Standby | 0 | 0 | 0.2 | 0 | 0 | 0.17
49 | P-206B | Hotwell slop oil pump B | P-206A/B | Pumps | 480 | DOL | MCC-101B | 0.75 |  | 0.16 | 0.22 | 0.8 | 0.76 | 0.2 | 0.17 | 0.27 | Continuous | 0.2 | 0 | 0 | 0.17 | 0 | 0
50 | K-101A | H-101 forced-draft fan A | K-101A/B | Fired-heater fans | 480 | DOL | MCC-101A | 90 |  | 73.72 | 0.82 | 0.935 | 0.86 | 78.84 | 46.78 | 91.68 | Standby | 0 | 0 | 78.84 | 0 | 0 | 46.78
51 | K-101B | H-101 forced-draft fan B | K-101A/B | Fired-heater fans | 480 | DOL | MCC-101B | 90 |  | 73.72 | 0.82 | 0.935 | 0.86 | 78.84 | 46.78 | 91.68 | Continuous | 78.84 | 0 | 0 | 46.78 | 0 | 0
52 | A-101-M1 | Atm. overhead condenser - fan motor 1/6 (VFD) | A-101 | Air-cooler fans | 480 | VFD | MCC-101A | 55 |  | 45 | 0.82 | 0.935 | 0.95 | 49.61 | 16.31 | 52.22 | Continuous | 49.61 | 0 | 0 | 16.31 | 0 | 0
53 | A-101-M2 | Atm. overhead condenser - fan motor 2/6 (VFD) | A-101 | Air-cooler fans | 480 | VFD | MCC-101B | 55 |  | 45 | 0.82 | 0.935 | 0.95 | 49.61 | 16.31 | 52.22 | Continuous | 49.61 | 0 | 0 | 16.31 | 0 | 0
54 | A-101-M3 | Atm. overhead condenser - fan motor 3/6 (VFD) | A-101 | Air-cooler fans | 480 | VFD | MCC-101A | 55 |  | 45 | 0.82 | 0.935 | 0.95 | 49.61 | 16.31 | 52.22 | Continuous | 49.61 | 0 | 0 | 16.31 | 0 | 0
55 | A-101-M4 | Atm. overhead condenser - fan motor 4/6 (VFD) | A-101 | Air-cooler fans | 480 | VFD | MCC-101B | 55 |  | 45 | 0.82 | 0.935 | 0.95 | 49.61 | 16.31 | 52.22 | Continuous | 49.61 | 0 | 0 | 16.31 | 0 | 0
56 | A-101-M5 | Atm. overhead condenser - fan motor 5/6 (VFD) | A-101 | Air-cooler fans | 480 | VFD | MCC-101A | 55 |  | 45 | 0.82 | 0.935 | 0.95 | 49.61 | 16.31 | 52.22 | Continuous | 49.61 | 0 | 0 | 16.31 | 0 | 0
57 | A-101-M6 | Atm. overhead condenser - fan motor 6/6 (VFD) | A-101 | Air-cooler fans | 480 | VFD | MCC-101B | 55 |  | 45 | 0.82 | 0.935 | 0.95 | 49.61 | 16.31 | 52.22 | Continuous | 49.61 | 0 | 0 | 16.31 | 0 | 0
58 | A-103-M1 | Kero cooler - fan motor 1/2 | A-103 | Air-cooler fans | 480 | DOL | MCC-101A | 11 |  | 7.5 | 0.68 | 0.91 | 0.85 | 8.24 | 5.11 | 9.7 | Continuous | 8.24 | 0 | 0 | 5.11 | 0 | 0
59 | A-103-M2 | Kero cooler - fan motor 2/2 | A-103 | Air-cooler fans | 480 | DOL | MCC-101B | 11 |  | 7.5 | 0.68 | 0.91 | 0.85 | 8.24 | 5.11 | 9.7 | Continuous | 8.24 | 0 | 0 | 5.11 | 0 | 0
60 | A-104-M1 | Diesel cooler - fan motor 1/2 | A-104 | Air-cooler fans | 480 | DOL | MCC-101A | 18.5 |  | 14.89 | 0.81 | 0.91 | 0.85 | 16.37 | 10.14 | 19.26 | Continuous | 16.37 | 0 | 0 | 10.14 | 0 | 0
61 | A-104-M2 | Diesel cooler - fan motor 2/2 | A-104 | Air-cooler fans | 480 | DOL | MCC-101B | 18.5 |  | 14.89 | 0.81 | 0.91 | 0.85 | 16.37 | 10.14 | 19.26 | Continuous | 16.37 | 0 | 0 | 10.14 | 0 | 0
62 | A-105-M1 | Ago cooler - fan motor 1/2 | A-105 | Air-cooler fans | 480 | DOL | MCC-101A | 30 |  | 24.23 | 0.81 | 0.91 | 0.85 | 26.63 | 16.5 | 31.33 | Continuous | 26.63 | 0 | 0 | 16.5 | 0 | 0
63 | A-105-M2 | Ago cooler - fan motor 2/2 | A-105 | Air-cooler fans | 480 | DOL | MCC-101B | 30 |  | 24.23 | 0.81 | 0.91 | 0.85 | 26.63 | 16.5 | 31.33 | Continuous | 26.63 | 0 | 0 | 16.5 | 0 | 0
64 | A-106-M1 | Stabiliser overhead condenser - fan motor 1/2 | A-106 | Air-cooler fans | 480 | DOL | MCC-101A | 11 |  | 8.55 | 0.78 | 0.91 | 0.85 | 9.4 | 5.83 | 11.06 | Continuous | 9.4 | 0 | 0 | 5.83 | 0 | 0
65 | A-106-M2 | Stabiliser overhead condenser - fan motor 2/2 | A-106 | Air-cooler fans | 480 | DOL | MCC-101B | 11 |  | 8.55 | 0.78 | 0.91 | 0.85 | 9.4 | 5.83 | 11.06 | Continuous | 9.4 | 0 | 0 | 5.83 | 0 | 0
66 | A-107-M1 | Splitter overhead condenser - fan motor 1/4 | A-107 | Air-cooler fans | 480 | DOL | MCC-101A | 30 |  | 19.25 | 0.64 | 0.91 | 0.85 | 21.16 | 13.11 | 24.89 | Continuous | 21.16 | 0 | 0 | 13.11 | 0 | 0
67 | A-107-M2 | Splitter overhead condenser - fan motor 2/4 | A-107 | Air-cooler fans | 480 | DOL | MCC-101B | 30 |  | 19.25 | 0.64 | 0.91 | 0.85 | 21.16 | 13.11 | 24.89 | Continuous | 21.16 | 0 | 0 | 13.11 | 0 | 0
68 | A-107-M3 | Splitter overhead condenser - fan motor 3/4 | A-107 | Air-cooler fans | 480 | DOL | MCC-101A | 30 |  | 19.25 | 0.64 | 0.91 | 0.85 | 21.16 | 13.11 | 24.89 | Continuous | 21.16 | 0 | 0 | 13.11 | 0 | 0
69 | A-107-M4 | Splitter overhead condenser - fan motor 4/4 | A-107 | Air-cooler fans | 480 | DOL | MCC-101B | 30 |  | 19.25 | 0.64 | 0.91 | 0.85 | 21.16 | 13.11 | 24.89 | Continuous | 21.16 | 0 | 0 | 13.11 | 0 | 0
70 | A-108-M1 | Heavy naphtha product cooler - fan motor 1/2 | A-108 | Air-cooler fans | 480 | DOL | MCC-101A | 30 |  | 23.23 | 0.77 | 0.91 | 0.85 | 25.53 | 15.82 | 30.04 | Continuous | 25.53 | 0 | 0 | 15.82 | 0 | 0
71 | A-108-M2 | Heavy naphtha product cooler - fan motor 2/2 | A-108 | Air-cooler fans | 480 | DOL | MCC-101B | 30 |  | 23.23 | 0.77 | 0.91 | 0.85 | 25.53 | 15.82 | 30.04 | Continuous | 25.53 | 0 | 0 | 15.82 | 0 | 0
72 | A-201-M1 | Lvgo cooler - fan motor 1/2 | A-201 | Air-cooler fans | 480 | DOL | MCC-101A | 15 |  | 12.4 | 0.83 | 0.91 | 0.85 | 13.62 | 8.44 | 16.02 | Continuous | 13.62 | 0 | 0 | 8.44 | 0 | 0
73 | A-201-M2 | Lvgo cooler - fan motor 2/2 | A-201 | Air-cooler fans | 480 | DOL | MCC-101B | 15 |  | 12.4 | 0.83 | 0.91 | 0.85 | 13.62 | 8.44 | 16.02 | Continuous | 13.62 | 0 | 0 | 8.44 | 0 | 0
74 | A-202-M1 | Hvgo Product cooler - fan motor 1/2 | A-202 | Air-cooler fans | 480 | DOL | MCC-101A | 37 |  | 26.56 | 0.72 | 0.935 | 0.86 | 28.41 | 16.86 | 33.03 | Continuous | 28.41 | 0 | 0 | 16.86 | 0 | 0
75 | A-202-M2 | Hvgo Product cooler - fan motor 2/2 | A-202 | Air-cooler fans | 480 | DOL | MCC-101B | 37 |  | 26.56 | 0.72 | 0.935 | 0.86 | 28.41 | 16.86 | 33.03 | Continuous | 28.41 | 0 | 0 | 16.86 | 0 | 0
76 | X-101-PA | Demulsifier injection package - metering pump A | X-101 | Chemical packages | 480 | DOL | MCC-101A | 0.75 |  | 0.45 | 0.6 | 0.8 | 0.76 | 0.56 | 0.48 | 0.74 | Standby | 0 | 0 | 0.56 | 0 | 0 | 0.48 | 2 x 100 % pumps per package
77 | X-101-PB | Demulsifier injection package - metering pump B | X-101 | Chemical packages | 480 | DOL | MCC-101B | 0.75 |  | 0.45 | 0.6 | 0.8 | 0.76 | 0.56 | 0.48 | 0.74 | Continuous | 0.56 | 0 | 0 | 0.48 | 0 | 0
78 | X-102-PA | Caustic injection package (desalted crude) - metering pump A | X-102 | Chemical packages | 480 | DOL | MCC-101A | 0.75 |  | 0.45 | 0.6 | 0.8 | 0.76 | 0.56 | 0.48 | 0.74 | Standby | 0 | 0 | 0.56 | 0 | 0 | 0.48 | 2 x 100 % pumps per package
79 | X-102-PB | Caustic injection package (desalted crude) - metering pump B | X-102 | Chemical packages | 480 | DOL | MCC-101B | 0.75 |  | 0.45 | 0.6 | 0.8 | 0.76 | 0.56 | 0.48 | 0.74 | Continuous | 0.56 | 0 | 0 | 0.48 | 0 | 0
80 | X-103-PA | Neutraliser / filming amine package (atm OH) - metering pump A | X-103 | Chemical packages | 480 | DOL | MCC-101A | 0.75 |  | 0.45 | 0.6 | 0.8 | 0.76 | 0.56 | 0.48 | 0.74 | Standby | 0 | 0 | 0.56 | 0 | 0 | 0.48 | 2 x 100 % pumps per package
81 | X-103-PB | Neutraliser / filming amine package (atm OH) - metering pump B | X-103 | Chemical packages | 480 | DOL | MCC-101B | 0.75 |  | 0.45 | 0.6 | 0.8 | 0.76 | 0.56 | 0.48 | 0.74 | Continuous | 0.56 | 0 | 0 | 0.48 | 0 | 0
82 | X-104-PA | Corrosion inhibitor package (VDU OH) - metering pump A | X-104 | Chemical packages | 480 | DOL | MCC-101A | 0.75 |  | 0.45 | 0.6 | 0.8 | 0.76 | 0.56 | 0.48 | 0.74 | Standby | 0 | 0 | 0.56 | 0 | 0 | 0.48 | 2 x 100 % pumps per package
83 | X-104-PB | Corrosion inhibitor package (VDU OH) - metering pump B | X-104 | Chemical packages | 480 | DOL | MCC-101B | 0.75 |  | 0.45 | 0.6 | 0.8 | 0.76 | 0.56 | 0.48 | 0.74 | Continuous | 0.56 | 0 | 0 | 0.48 | 0 | 0
84 | DT-101A1 | D-101A 1st stage - HV transformer 1/2 (150 kVA, 480 V / 13-23 kV) | D-101A | Desalter transformers | 480 | Feeder | MCC-101A | 127.5 | 150 | 44.62 | 0.35 | 1 | 0.85 | 44.62 | 27.66 | 52.5 | Continuous | 44.62 | 0 | 0 | 27.66 | 0 | 0 | Load factor 0.35 typical for electrostatic grids (vendor to confirm)
85 | DT-101A2 | D-101A 1st stage - HV transformer 2/2 (150 kVA, 480 V / 13-23 kV) | D-101A | Desalter transformers | 480 | Feeder | MCC-101B | 127.5 | 150 | 44.62 | 0.35 | 1 | 0.85 | 44.62 | 27.66 | 52.5 | Continuous | 44.62 | 0 | 0 | 27.66 | 0 | 0 | Load factor 0.35 typical for electrostatic grids (vendor to confirm)
86 | DT-101B1 | D-101B 2nd stage - HV transformer 1/2 (150 kVA, 480 V / 13-23 kV) | D-101B | Desalter transformers | 480 | Feeder | MCC-101A | 127.5 | 150 | 44.62 | 0.35 | 1 | 0.85 | 44.62 | 27.66 | 52.5 | Continuous | 44.62 | 0 | 0 | 27.66 | 0 | 0 | Load factor 0.35 typical for electrostatic grids (vendor to confirm)
87 | DT-101B2 | D-101B 2nd stage - HV transformer 2/2 (150 kVA, 480 V / 13-23 kV) | D-101B | Desalter transformers | 480 | Feeder | MCC-101B | 127.5 | 150 | 44.62 | 0.35 | 1 | 0.85 | 44.62 | 27.66 | 52.5 | Continuous | 44.62 | 0 | 0 | 27.66 | 0 | 0 | Load factor 0.35 typical for electrostatic grids (vendor to confirm)
88 | MOV-A | MOV / electric valve actuators - allowance (18 x 1.5 kW), bus A |  | Valve actuators | 480 | Feeder | MCC-101A | 27 |  | 27 | 1 | 1 | 0.75 | 27 | 23.81 | 36 | Intermittent | 0 | 27 | 0 | 0 | 23.81 | 0 | ROSOVs on hot/LPG pump suctions, BL & heater isolation
89 | MOV-B | MOV / electric valve actuators - allowance (18 x 1.5 kW), bus B |  | Valve actuators | 480 | Feeder | MCC-101B | 27 |  | 27 | 1 | 1 | 0.75 | 27 | 23.81 | 36 | Intermittent | 0 | 27 | 0 | 0 | 23.81 | 0 | ROSOVs on hot/LPG pump suctions, BL & heater isolation
90 | HTP-101 | Electric heat tracing panel - CDU slop & HN lines (allowance) |  | Heat tracing | 480 | Feeder | MCC-101A | 30 |  | 21 | 0.7 | 1 | 1 | 21 | 0 | 21 | Continuous | 21 | 0 | 0 | 0 | 0 | 0 | Self-regulating; winter design -5 C; steam tracing elsewhere
91 | HTP-102 | Electric heat tracing panel - VDU slop wax / slop oil lines (allowance) |  | Heat tracing | 480 | Feeder | MCC-101B | 40 |  | 28 | 0.7 | 1 | 1 | 28 | 0 | 28 | Continuous | 28 | 0 | 0 | 0 | 0 | 0
92 | AH-101 | Analyser house AH-101 HVAC & utilities (analysers on UPS) |  | HVAC | 480 | Feeder | MCC-101B | 15 |  | 12 | 0.8 | 1 | 0.85 | 12 | 7.44 | 14.12 | Continuous | 12 | 0 | 0 | 7.44 | 0 | 0
93 | BEF-101A | SS-100 battery-room exhaust fan A |  | HVAC | 480 | Feeder | MCC-101A | 1.1 |  | 1.1 | 1 | 1 | 0.8 | 1.1 | 0.82 | 1.38 | Continuous | 1.1 | 0 | 0 | 0.82 | 0 | 0
94 | BEF-101B | SS-100 battery-room exhaust fan B |  | HVAC | 480 | Feeder | MCC-101B | 1.1 |  | 1.1 | 1 | 1 | 0.8 | 1.1 | 0.82 | 1.38 | Standby | 0 | 0 | 1.1 | 0 | 0 | 0.82
95 | HVAC-101A | SS-100 HVAC package A (2 x 100 %) |  | HVAC | 480 | Feeder | MCC-101A | 60 |  | 48 | 0.8 | 1 | 0.85 | 48 | 29.75 | 56.47 | Continuous | 48 | 0 | 0 | 29.75 | 0 | 0
96 | HVAC-101B | SS-100 HVAC package B (2 x 100 %) |  | HVAC | 480 | Feeder | MCC-101B | 60 |  | 48 | 0.8 | 1 | 0.85 | 48 | 29.75 | 56.47 | Standby | 0 | 0 | 48 | 0 | 0 | 29.75
97 | HVAC-102A | FAR-100 HVAC package A (2 x 100 %) |  | HVAC | 480 | Feeder | MCC-101A | 25 |  | 20 | 0.8 | 1 | 0.85 | 20 | 12.39 | 23.53 | Continuous | 20 | 0 | 0 | 12.39 | 0 | 0
98 | HVAC-102B | FAR-100 HVAC package B (2 x 100 %) |  | HVAC | 480 | Feeder | MCC-101B | 25 |  | 20 | 0.8 | 1 | 0.85 | 20 | 12.39 | 23.53 | Standby | 0 | 0 | 20 | 0 | 0 | 12.39
99 | CR-A | Field convenience receptacles (120 V), via LTR-101A |  | Lighting & small power | 208 | Feeder (via LTR) | MCC-101A | 10 |  | 10 | 1 | 1 | 0.9 | 10 | 4.84 | 11.11 | Intermittent | 0 | 10 | 0 | 0 | 4.84 | 0
100 | CR-B | Field convenience receptacles (120 V), via LTR-101B |  | Lighting & small power | 208 | Feeder (via LTR) | MCC-101B | 10 |  | 10 | 1 | 1 | 0.9 | 10 | 4.84 | 11.11 | Intermittent | 0 | 10 | 0 | 0 | 4.84 | 0
101 | LTG-A | Area & structure lighting (LED), via LTR-101A 480-208Y/120 V |  | Lighting & small power | 208 | Feeder (via LTR) | MCC-101A | 24 |  | 24 | 1 | 1 | 0.95 | 24 | 7.89 | 25.26 | Continuous | 24 | 0 | 0 | 7.89 | 0 | 0
102 | LTG-B | Area & structure lighting (LED), via LTR-101B 480-208Y/120 V |  | Lighting & small power | 208 | Feeder (via LTR) | MCC-101B | 24 |  | 24 | 1 | 1 | 0.95 | 24 | 7.89 | 25.26 | Continuous | 24 | 0 | 0 | 7.89 | 0 | 0
103 | LTG-BA | Building lighting SS-100 / FAR-100, via LTR-101A |  | Lighting & small power | 208 | Feeder (via LTR) | MCC-101A | 5 |  | 5 | 1 | 1 | 0.95 | 5 | 1.64 | 5.26 | Continuous | 5 | 0 | 0 | 1.64 | 0 | 0
104 | LTG-BB | Building lighting SS-100 / FAR-100, via LTR-101B |  | Lighting & small power | 208 | Feeder (via LTR) | MCC-101B | 5 |  | 5 | 1 | 1 | 0.95 | 5 | 1.64 | 5.26 | Continuous | 5 | 0 | 0 | 1.64 | 0 | 0
105 | SP-A | Building small power & receptacles, via LTR-101A |  | Lighting & small power | 208 | Feeder (via LTR) | MCC-101A | 10 |  | 6 | 0.6 | 1 | 0.9 | 6 | 2.91 | 6.67 | Continuous | 6 | 0 | 0 | 2.91 | 0 | 0
106 | SP-B | Building small power & receptacles, via LTR-101B |  | Lighting & small power | 208 | Feeder (via LTR) | MCC-101B | 10 |  | 6 | 0.6 | 1 | 0.9 | 6 | 2.91 | 6.67 | Continuous | 6 | 0 | 0 | 2.91 | 0 | 0
107 | WR-A | Welding receptacles 3 x 63 A, 480 V, bus A |  | Welding outlets | 480 | Feeder | MCC-101A | 75 |  | 75 | 1 | 1 | 0.7 | 75 | 76.52 | 107.14 | Intermittent | 0 | 75 | 0 | 0 | 76.52 | 0
108 | WR-B | Welding receptacles 3 x 63 A, 480 V, bus B |  | Welding outlets | 480 | Feeder | MCC-101B | 75 |  | 75 | 1 | 1 | 0.7 | 75 | 76.52 | 107.14 | Intermittent | 0 | 75 | 0 | 0 | 76.52 | 0
109 | CP-101 | Cathodic protection transformer-rectifier (buried piping / tank bottoms in plot) |  | Cathodic protection | 480 | Feeder | MCC-101A | 8 |  | 6.4 | 0.8 | 1 | 0.8 | 6.4 | 4.8 | 8 | Continuous | 6.4 | 0 | 0 | 4.8 | 0 | 0
110 | BC-101A | 125 V DC battery charger A (switchgear control), 2 x 100 % |  | UPS / DC | 480 | Feeder | MCC-101A | 6 |  | 3 | 0.5 | 0.9 | 0.85 | 3.33 | 2.07 | 3.92 | Continuous | 3.33 | 0 | 0 | 2.07 | 0 | 0
111 | BC-101B | 125 V DC battery charger B (switchgear control), 2 x 100 % |  | UPS / DC | 480 | Feeder | MCC-101B | 6 |  | 3 | 0.5 | 0.9 | 0.85 | 3.33 | 2.07 | 3.92 | Continuous | 3.33 | 0 | 0 | 2.07 | 0 | 0
112 | UPS-101A | UPS-101A rectifier input (2 x 100 % 100 kVA, 50 % share + battery recharge) |  | UPS / DC | 480 | Feeder | MCC-101A | 34.03 |  | 34.03 | 1 | 1 | 0.95 | 34.03 | 11.19 | 35.82 | Continuous | 34.03 | 0 | 0 | 11.19 | 0 | 0
113 | UPS-101B | UPS-101B rectifier input (2 x 100 % 100 kVA, 50 % share + battery recharge) |  | UPS / DC | 480 | Feeder | MCC-101B | 34.03 |  | 34.03 | 1 | 1 | 0.95 | 34.03 | 11.19 | 35.82 | Continuous | 34.03 | 0 | 0 | 11.19 | 0 | 0
114 | HST-101 | Monorail hoists P-101/P-102 maintenance (2 x 7.5 kW) |  | Miscellaneous | 480 | Feeder | MCC-101A | 15 |  | 15 | 1 | 1 | 0.8 | 15 | 11.25 | 18.75 | Intermittent | 0 | 15 | 0 | 0 | 11.25 | 0
115 | SB-101 | H-101 convection sootblowers (8 x 0.75 kW, electric retract) | H-101 | Miscellaneous | 480 | Feeder | MCC-101B | 6 |  | 6 | 1 | 1 | 0.8 | 6 | 4.5 | 7.5 | Intermittent | 0 | 6 | 0 | 0 | 4.5 | 0
TOTAL (all buses)
Maximum demand per bus = C + 0.3 x I + 0.1 x S (kW and kvar separately), kVA = vector sum
| Bus |  | MD kW (formula) | MD kvar (formula) | MD kVA (formula)
MCC-101A
MCC-101B
SWG-102A
SWG-102B

## Bus Summary
100 kBPSD Crude & Vacuum Distillation Unit - Maximum Demand per Bus
CFU-000-EL-LDL-001 Rev A (Issued for review (FEED)), 2026-10-02 ¦ Generic Refinery - Gulf Coast
Bus | kV | No. loads | Connected kW | C kW | I kW | S kW | MD kW | MD kvar | MD kVA | PF
MCC-101A | 0.48 | 52 | 1786.7926 | 1092.7344 | 127 | 567.0582 | 1187.5402 | 649.3892 | 1353.4984 | 0.87739
MCC-101B | 0.48 | 53 | 1796.5081 | 1088.0162 | 124.1155 | 584.3764 | 1183.6885 | 640.017 | 1345.6375 | 0.87965
SWG-102A | 4.16 | 5 | 1903.1541 | 984.8092 | 0 | 918.3449 | 1076.6437 | 528.2045 | 1199.2338 | 0.89778
SWG-102B | 4.16 | 5 | 1903.1541 | 918.3449 | 0 | 984.8092 | 1016.8258 | 533.6884 | 1148.3719 | 0.88545
SWG-102A incl. LV through-load | 4.16 | [5 empty] | 2276.0593 | 1203.5693 | 2574.6893 | 0.88401
SWG-102B incl. LV through-load | 4.16 | [5 empty] | 2212.3512 | 1199.3062 | 2516.5121 | 0.87913
SWG-101A | 13.8 | [5 empty] | 2294.2678 | 1275.7834 | 2625.1263 | 0.87396
SWG-101B | 13.8 | [5 empty] | 2230.05 | 1271.2645 | 2566.9508 | 0.86875
LV total (MCC-101A+B) | 0.48 | 105 | 3583.3007 | 2180.7506 | 251.1155 | 1151.4346 | 2371.2287 | 1289.4062 | 2699.1284 | 0.87852
MV motors total (SWG-102A+B) | 4.16 | 10 | 3806.3082 | 1903.1541 | 0 | 1903.1541 | 2093.4695 | 1061.893 | 2347.3882 | 0.89183
UNIT TOTAL at 13.8 kV (incl. TR losses) | 13.8 | 115 |  |  |  |  | 4524.3178 | 2547.048 | 5192.004 | 0.8714
Transformers
Tag | Ratio | ONAN kVA | ONAF kVA | Z % | MD kVA (one TR, tie closed) | MD x 1.25 kVA | Loading at MD % ONAN | Cooling | Vector | Neutral
TR-101 / TR-102 | 13.8/4.16 kV | 7500 | 9375 | 7 | 5091.1334 | 6363.9168 | 67.8818 | ONAN/ONAF | Dyn1 | Low-resistance grounded, NGR 400 A / 10 s
TR-103 / TR-104 | 4.16/0.48 kV | 3000 | 3750 | 5.75 | 2699.1284 | 3373.9105 | 89.9709 | ONAN/ONAF | Dyn1 | High-resistance grounded, NGR 5 A (continuous), ground-fault alarm
LTR-101A | 0.48/0.208 kV | 75 |  | 4 | 40.5263 | 50.6579 | 54.0351 | Dry type (AN) | Dyn1 | Solidly grounded
LTR-101B | 0.48/0.208 kV | 75 |  | 4 | 40.5263 | 50.6579 | 54.0351 | Dry type (AN) | Dyn1 | Solidly grounded

## UPS Loads
100 kBPSD Crude & Vacuum Distillation Unit - UPS (120 V) Consumers
CFU-000-EL-LDL-001 Rev A (Issued for review (FEED)), 2026-10-02 ¦ Generic Refinery - Gulf Coast
Tag | Description | UPS bus | Consumer total kVA | This feed kVA (50 %) | This feed kW | PF
UPS-DCS-A | Distributed control system (controllers, I/O, servers, HMI in FAR) - feed A (dual redundant PSU, 50 % normal share) | UDB-101A | 22 | 11 | 9.9 | 0.9
UPS-DCS-B | Distributed control system (controllers, I/O, servers, HMI in FAR) - feed B (dual redundant PSU, 50 % normal share) | UDB-101B | 22 | 11 | 9.9 | 0.9
UPS-SIS-A | Safety instrumented system incl. H-101/H-201 BMS, ESD solenoids - feed A (dual redundant PSU, 50 % normal share) | UDB-101A | 14 | 7 | 6.3 | 0.9
UPS-SIS-B | Safety instrumented system incl. H-101/H-201 BMS, ESD solenoids - feed B (dual redundant PSU, 50 % normal share) | UDB-101B | 14 | 7 | 6.3 | 0.9
UPS-FGS-A | Fire & gas system incl. detectors/beacons - feed A (dual redundant PSU, 50 % normal share) | UDB-101A | 6 | 3 | 2.7 | 0.9
UPS-FGS-B | Fire & gas system incl. detectors/beacons - feed B (dual redundant PSU, 50 % normal share) | UDB-101B | 6 | 3 | 2.7 | 0.9
UPS-TEL-A | Telecom: PAGA, CCTV, LAN/fibre, radio - feed A (dual redundant PSU, 50 % normal share) | UDB-101A | 8 | 4 | 3.6 | 0.9
UPS-TEL-B | Telecom: PAGA, CCTV, LAN/fibre, radio - feed B (dual redundant PSU, 50 % normal share) | UDB-101B | 8 | 4 | 3.6 | 0.9
UPS-ANZ-A | Process analysers (AH-101) - feed A (dual redundant PSU, 50 % normal share) | UDB-101A | 6 | 3 | 2.7 | 0.9
UPS-ANZ-B | Process analysers (AH-101) - feed B (dual redundant PSU, 50 % normal share) | UDB-101B | 6 | 3 | 2.7 | 0.9
UPS-MISC-A | Misc. instrument panels, MCC/IED networking, metering - feed A (dual redundant PSU, 50 % normal share) | UDB-101A | 4 | 2 | 1.8 | 0.9
UPS-MISC-B | Misc. instrument panels, MCC/IED networking, metering - feed B (dual redundant PSU, 50 % normal share) | UDB-101B | 4 | 2 | 1.8 | 0.9

## Basis
100 kBPSD Crude & Vacuum Distillation Unit - Load List Basis
CFU-000-EL-LDL-001 Rev A (Issued for review (FEED)), 2026-10-02 ¦ Generic Refinery - Gulf Coast
1. Sources: motor ratings, absorbed power, fan counts and package data from data/equipment.json (process/mechanical sizing). Absorbed power used where available; 'Input kW' = absorbed / efficiency (/ VFD efficiency 0.97 where applicable).
2. Voltage levels: motors >= 200 kW at 4.16 kV (VCB, DOL unless VFD); motors < 200 kW at 480 V (MCC, DOL). VFDs: A-101 overhead condenser fans (4 x 90 kW, process temperature control and energy) and H-101 ID fans K-102A/B (draft control, 4.16 kV MV drive).
3. Efficiency / PF by motor size (NEMA Premium / IEEE 841 typical): <=1.5 kW 0.80/0.76; <=7.5 kW 0.875/0.82; <=30 kW 0.91/0.85; <=90 kW 0.935/0.86; <=160 kW 0.95/0.87; LV >160 kW 0.955/0.87; MV <500 kW 0.955/0.87; MV >=500 kW 0.965/0.89. VFD supply PF 0.95.
4. Duty: C = continuous, I = intermittent, S = standby. Pump pairs A/B (2 x 100 %): A always on bus A, B on bus B; the normally running unit of each pair (C) is chosen to balance the two bus sections, the other is standby (S). Air-cooler fans all continuous, split alternately across the buses.
5. Maximum demand (IEEE 141 / IEC style diversity): MD = 1.0 C + 0.3 I + 0.1 S, applied to kW and kvar separately; kVA by vector sum.
6. Allowances (no process data available - FEED assumptions, to be replaced by vendor data): MOV/actuators 36 x 1.5 kW; heat tracing 70 kW (slop/HN/slop-wax lines); lighting 2 x 29 kW LED + building lighting; small power/receptacles; welding receptacles 6 x 63 A; SS-100 HVAC 2 x 60 kW, FAR-100 HVAC 2 x 25 kW; cathodic protection 8 kW; analyser house 15 kW; UPS loads 60 kVA; 125 V DC chargers 2 x 6 kW.
7. Desalter transformers: 2 x 150 kVA per stage (D-101A, D-101B), 480 V primary, load factor 0.35 (vendor to confirm), PF 0.85; one transformer of each stage on each bus.
8. Chemical injection packages X-101..X-104: 2 x 100 % metering pumps 0.75 kW each, absorbed 60 %.
9. 208 V loads are supplied via lighting transformers LTR-101A/B (480-208Y/120 V) from MCC-101A/B.
10. UPS consumers (120 V) are listed separately; they are supplied through UPS-101A/B whose rectifier input (incl. battery recharge) appears on MCC-101A/B. Not double counted.