## Summary
CFU-000-IC-IOL-001 I/O LIST - SUMMARY (Rev A, FEED)
100 kBPSD Crude & Vacuum Distillation Unit - derived from data/instruments.json; spare >= 20 % installed
Controller | System | AI used | AI inst. | AO used | AO inst. | DI used | DI inst. | DO used | DO inst. | Total used | Total installed | Spare % | Cards AI/AO/DI/DO
CDU-1 | DCS | 72 | 96 | 31 | 48 | 35 | 64 | 35 | 48 | 173 | 256 | 48 | 6/6/2/3
CDU-2 | DCS | 78 | 96 | 29 | 40 | 67 | 96 | 66 | 96 | 240 | 328 | 36.7 | 6/5/3/6
VDU | DCS | 47 | 64 | 22 | 32 | 28 | 64 | 28 | 48 | 125 | 208 | 66.4 | 4/4/2/3
SIS-1 | SIS | 6 | 16 | 0 | 0 | 15 | 32 | 16 | 32 | 37 | 80 | 116.2 | 1/0/1/2
BMS-H101 | BMS | 33 | 48 | 0 | 0 | 24 | 32 | 4 | 16 | 61 | 96 | 57.4 | 3/0/1/1
BMS-H201 | BMS | 15 | 32 | 0 | 0 | 12 | 32 | 3 | 16 | 30 | 80 | 166.7 | 2/0/1/1
FGS-1 | F&G | 135 | 176 | 0 | 0 | 37 | 64 | 22 | 32 | 194 | 272 | 40.2 | 11/0/2/2
Totals per system
System | AI | AO | DI | DO | Used | Installed
DCS | 197 | 82 | 130 | 129 | 538 | 792
SIS | 6 | 0 | 15 | 16 | 37 | 80
BMS | 48 | 0 | 36 | 7 | 91 | 176
F&G | 135 | 0 | 37 | 22 | 194 | 272
GRAND TOTAL |  |  |  |  | 860 | 1320
Points by source
instrument index | 462
I&C addition (add to index) | 17
equipment.json (MCC hardwired interface) | 256
C&E CFU-000-IC-CE-001 | 8
F&G allowance (mapping study) | 117

## I-O List
Tag | Parent tag | Type | Service | Loop | P&ID | System | Controller | I/O | Signal | I/O card | Ch. | FAR-100 cabinet | Marsh. terminals | JB | JB term. | Multicore | Pair | MC length m | Zone | Equipment | SIF | SIL | Range | Units | Source
AT-1046 | AT-1046 | Analyser transmitter | Salt-in-crude analyser, desalted crude | AT-1046 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 1 | FAR-100/MC-CDU-1-A01 | TB01-1/2 | JB-DA-A2 | 1/2 | MC-DA-A2 | 1 | 90 | A2 | D-101A |  |  | 0-50 | PTB | instrument index
AT-1046 | AT-1046 | Analyser transmitter | Salt-in-crude, desalted crude | AT-1046 | (P&ID sheet 002) | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 2 | FAR-100/MC-CDU-1-A01 | TB01-3/4 | JB-DA-A2 | 3/4 | MC-DA-A2 | 2 | 90 | A2 | D-101A |  |  |  |  | I&C addition (add to index)
AT-1047 | AT-1047 | Analyser transmitter | BS&W analyser (microwave water-cut), desalted crude | AT-1047 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 3 | FAR-100/MC-CDU-1-A01 | TB01-5/6 | JB-DA-A2 | 5/6 | MC-DA-A2 | 3 | 90 | A2 | D-101A |  |  | 0-2 | vol% BS&W | instrument index
AT-1047 | AT-1047 | Analyser transmitter | BS&W, desalted crude | AT-1047 | (P&ID sheet 002) | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 4 | FAR-100/MC-CDU-1-A01 | TB01-7/8 | JB-DA-A2 | 7/8 | MC-DA-A2 | 4 | 90 | A2 | D-101A |  |  |  |  | I&C addition (add to index)
AT-1049 | AT-1049 | Analyser transmitter | Oil-in-water analyser, desalter brine | AT-1049 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 5 | FAR-100/MC-CDU-1-A01 | TB01-9/10 | JB-DA-A2 | 9/10 | MC-DA-A2 | 5 | 90 | A2 | D-101A |  |  | 0-500 | ppmw oil | instrument index
AT-1049 | AT-1049 | Analyser transmitter | Oil-in-water, desalter brine | AT-1049 | (P&ID sheet 002) | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 6 | FAR-100/MC-CDU-1-A01 | TB01-11/12 | JB-DA-A2 | 11/12 | MC-DA-A2 | 6 | 90 | A2 | D-101A |  |  |  |  | I&C addition (add to index)
LT-1007 | LT-1007 | Level transmitter | D-101A water/oil interface | LIC-1007 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 7 | FAR-100/MC-CDU-1-A01 | TB01-13/14 | JB-DA-A2 | 13/14 | MC-DA-A2 | 7 | 90 | A2 | D-101A |  |  | 0-100 | % | instrument index
LT-1008 | LT-1008 | Level transmitter | D-101B water/oil interface | LIC-1008 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 8 | FAR-100/MC-CDU-1-A01 | TB01-15/16 | JB-DA-A2 | 15/16 | MC-DA-A2 | 8 | 80 | A2 | D-101B |  |  | 0-100 | % | instrument index
PDT-1005 | PDT-1005 | Differential pressure transmitter | 1st-stage mix valve dP | PDIC-1005 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 9 | FAR-100/MC-CDU-1-A01 | TB01-17/18 | JB-DA-A2 | 21/22 | MC-DA-A2 | 11 | 90 | A2 | D-101A |  |  | 0-2.5 | bar | instrument index
PDT-1006 | PDT-1006 | Differential pressure transmitter | 2nd-stage mix valve dP | PDIC-1006 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 10 | FAR-100/MC-CDU-1-A01 | TB01-19/20 | JB-DA-A2 | 23/24 | MC-DA-A2 | 12 | 80 | A2 | D-101B |  |  | 0-2.5 | bar | instrument index
PI-1210 | PI-1210 | Pressure gauge | D-101A pressure | PI-1210 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 11 | FAR-100/MC-CDU-1-A01 | TB01-21/22 | JB-DA-A2 | 29/30 | MC-DA-A2 | 15 | 90 | A2 | D-101A |  |  | 0-5 | barg | instrument index
PI-1211 | PI-1211 | Pressure gauge | D-101B pressure | PI-1211 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 12 | FAR-100/MC-CDU-1-A01 | TB01-23/24 | JB-DA-A2 | 31/32 | MC-DA-A2 | 16 | 80 | A2 | D-101B |  |  | 0-5 | barg | instrument index
PT-1009 | PT-1009 | Pressure transmitter | Desalter pressure (above crude vapour pressure) | PIC-1009 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI01 | 13 | FAR-100/MC-CDU-1-A01 | TB01-25/26 | JB-DA-A2 | 33/34 | MC-DA-A2 | 17 | 80 | A2 | D-101B |  |  | 0-15 | barg | instrument index
TI-1209 | TI-1209 | Temperature indicator | Desalted crude temperature | TI-1209 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 1 | FAR-100/MC-CDU-1-A01 | TB02-1/2 | JB-DA-A2 | 37/38 | MC-DA-A2 | 19 | 90 | A2 | D-101A |  |  | 0-200 | C | instrument index
TI-1212 | TI-1212 | Temperature indicator | Brine to WWT temperature | TI-1212 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 2 | FAR-100/MC-CDU-1-A01 | TB02-3/4 | JB-DA-A2 | 39/40 | MC-DA-A2 | 20 | 90 | A2 | D-101A |  |  | 0-200 | C | instrument index
TI-1215 | TI-1215 | Temperature indicator | Wash water to desalter temperature | TI-1215 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 3 | FAR-100/MC-CDU-1-A01 | TB02-5/6 | JB-DA-A2 | 41/42 | MC-DA-A2 | 21 | 90 | A2 | D-101A |  |  | 0-200 | C | instrument index
TT-1004 | TT-1004 | Temperature transmitter | Desalter inlet temperature | TIC-1004 | CFU-100-PR-PID-001 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 4 | FAR-100/MC-CDU-1-A01 | TB02-7/8 | JB-DA-A2 | 43/44 | MC-DA-A2 | 22 | 90 | A2 | D-101A |  |  | 0-200 | C | instrument index
AT-1048 | AT-1048 | Analyser transmitter | Crude API / density, salt, BS&W at charge (crude-switch DV) | AT-1048 | CFU-100-PR-PID-001 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 5 | FAR-100/MC-CDU-1-A01 | TB02-9/10 | JB-DA-A3 | 1/2 | MC-DA-A3 | 1 | 160 | A3 | P-101A |  |  | 20-45 | API | instrument index
AT-1048 | AT-1048 | Analyser transmitter | Crude API / density, salt, BS&W at charge (crude switch DV) | AT-1048 | (P&ID sheet 001) | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 6 | FAR-100/MC-CDU-1-A01 | TB02-11/12 | JB-DA-A3 | 3/4 | MC-DA-A3 | 2 | 160 | A3 | P-101A |  |  |  |  | I&C addition (add to index)
FT-1001 | FT-1001 | Flow transmitter | Crude charge flow (unit throughput) | FIC-1001 | CFU-100-PR-PID-001 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 7 | FAR-100/MC-CDU-1-A01 | TB02-13/14 | JB-DA-A3 | 5/6 | MC-DA-A3 | 3 | 160 | A3 | P-101A |  |  | 0-1000 | m3/h | instrument index
FT-1003 | FT-1003 | Flow transmitter | Wash water ratio to crude (5 LV%) | FFIC-1003 | CFU-100-PR-PID-002 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 8 | FAR-100/MC-CDU-1-A01 | TB02-15/16 | JB-DA-A3 | 7/8 | MC-DA-A3 | 4 | 120 | A3 | P-114A |  |  | 0-50 | m3/h | instrument index
TT-1041 | TT-1041 | Temperature transmitter | TPA return temperature (duty) | TIC-1041 | CFU-100-PR-PID-001 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 9 | FAR-100/MC-CDU-1-A01 | TB02-17/18 | JB-DA-A3 | 13/14 | MC-DA-A3 | 7 | 160 | A3 | P-101A |  |  | 0-150 | C | instrument index
TI-1202 | TI-1202 | Temperature indicator | Crude E-101 outlet | TI-1202 | CFU-100-PR-PID-001 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 10 | FAR-100/MC-CDU-1-A01 | TB02-19/20 | JB-DA-A4 | 1/2 | MC-DA-A4 | 1 | 180 | A4 | E-101 |  |  | 0-120 | C | instrument index
TI-1203 | TI-1203 | Temperature indicator | Crude E-102 outlet | TI-1203 | CFU-100-PR-PID-001 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 11 | FAR-100/MC-CDU-1-A01 | TB02-21/22 | JB-DA-A4 | 3/4 | MC-DA-A4 | 2 | 180 | A4 | E-102 |  |  | 0-150 | C | instrument index
TI-1204 | TI-1204 | Temperature indicator | Crude E-103 outlet | TI-1204 | CFU-100-PR-PID-001 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 12 | FAR-100/MC-CDU-1-A01 | TB02-23/24 | JB-DA-A4 | 5/6 | MC-DA-A4 | 3 | 170 | A4 | E-103A |  |  | 0-200 | C | instrument index
TI-1205 | TI-1205 | Temperature indicator | Crude E-104 outlet | TI-1205 | CFU-100-PR-PID-001 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI02 | 13 | FAR-100/MC-CDU-1-A01 | TB02-25/26 | JB-DA-A4 | 7/8 | MC-DA-A4 | 4 | 160 | A4 | E-104 |  |  | 0-200 | C | instrument index
TI-1206 | TI-1206 | Temperature indicator | Crude E-105 outlet | TI-1206 | CFU-100-PR-PID-001 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 1 | FAR-100/MC-CDU-1-A01 | TB03-1/2 | JB-DA-A4 | 9/10 | MC-DA-A4 | 5 | 160 | A4 | E-105 |  |  | 0-200 | C | instrument index
TI-1217 | TI-1217 | Temperature indicator | Crude E-106 outlet | TI-1217 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 2 | FAR-100/MC-CDU-1-A01 | TB03-3/4 | JB-DA-A4 | 11/12 | MC-DA-A4 | 6 | 170 | A4 | E-106A |  |  | 0-250 | C | instrument index
TI-1218 | TI-1218 | Temperature indicator | Crude E-107 outlet | TI-1218 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 3 | FAR-100/MC-CDU-1-A01 | TB03-5/6 | JB-DA-A4 | 13/14 | MC-DA-A4 | 7 | 160 | A4 | E-107 |  |  | 0-250 | C | instrument index
TI-1219 | TI-1219 | Temperature indicator | Crude E-108 outlet | TI-1219 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 4 | FAR-100/MC-CDU-1-A01 | TB03-7/8 | JB-DA-A4 | 15/16 | MC-DA-A4 | 8 | 160 | A4 | E-108A |  |  | 0-400 | C | instrument index
TI-1220 | TI-1220 | Temperature indicator | Crude E-109 outlet | TI-1220 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 5 | FAR-100/MC-CDU-1-A01 | TB03-9/10 | JB-DA-A4 | 17/18 | MC-DA-A4 | 9 | 140 | A4 | E-109 |  |  | 0-400 | C | instrument index
TI-1222 | TI-1222 | Temperature indicator | Crude E-111 outlet | TI-1222 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 6 | FAR-100/MC-CDU-1-A01 | TB03-11/12 | JB-DA-A4 | 19/20 | MC-DA-A4 | 10 | 190 | A4 | E-111A |  |  | 0-400 | C | instrument index
TT-1043 | TT-1043 | Temperature transmitter | MPA return temperature | TIC-1043 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 7 | FAR-100/MC-CDU-1-A01 | TB03-13/14 | JB-DA-A4 | 21/22 | MC-DA-A4 | 11 | 160 | A4 | E-108A |  |  | 0-250 | C | instrument index
TT-1045 | TT-1045 | Temperature transmitter | BPA return temperature | TIC-1045 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 8 | FAR-100/MC-CDU-1-A01 | TB03-15/16 | JB-DA-A4 | 23/24 | MC-DA-A4 | 12 | 160 | A4 | E-108A |  |  | 0-300 | C | instrument index
LT-1110 | LT-1110 | Level transmitter | E-113 steam-generator level | LIC-1110 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 9 | FAR-100/MC-CDU-1-A01 | TB03-17/18 | JB-DA-B4-2 | 5/6 | MC-DA-B4-2 | 3 | 160 | B4 | E-113 |  |  | 0-100 | % | instrument index
PT-1111 | PT-1111 | Pressure transmitter | E-113 MP steam pressure | PIC-1111 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 10 | FAR-100/MC-CDU-1-A01 | TB03-19/20 | JB-DA-B4-2 | 27/28 | MC-DA-B4-2 | 14 | 160 | B4 | E-113 |  |  | 0-20 | barg | instrument index
TI-1221 | TI-1221 | Temperature indicator | Crude E-110 outlet | TI-1221 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 11 | FAR-100/MC-CDU-1-A01 | TB03-21/22 | JB-DA-B4-2 | 37/38 | MC-DA-B4-2 | 19 | 130 | B4 | E-110A |  |  | 0-400 | C | instrument index
AT-1021 | AT-1021 | Analyser transmitter | Fuel gas Wobbe index / LHV analyser (calorimeter), FG header | PIC-1021 | CFU-900-PR-PID-016 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 12 | FAR-100/MC-CDU-1-A01 | TB03-23/24 | JB-DA-C2-1 | 1/2 | MC-DA-C2-1 | 1 | 100 | C2 | H-101 |  |  | 40-55 | MJ/Sm3 (Wobbe) | instrument index
AT-1022 | AT-1022 | Analyser transmitter | H-101 arch O2 / CO analyser | AIC-1022 | CFU-100-PR-PID-005 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI03 | 13 | FAR-100/MC-CDU-1-A01 | TB03-25/26 | JB-DA-C2-1 | 3/4 | MC-DA-C2-1 | 2 | 100 | C2 | H-101 |  |  | 0-10 | vol% O2 | instrument index
FT-1011 | FT-1011 | Flow transmitter | H-101 pass 1 flow | FIC-1011 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 1 | FAR-100/MC-CDU-1-A01 | TB04-1/2 | JB-DA-C2-1 | 5/6 | MC-DA-C2-1 | 3 | 100 | C2 | H-101 |  |  | 0-100000 | kg/h | instrument index
FT-1012 | FT-1012 | Flow transmitter | H-101 pass 2 flow | FIC-1012 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 2 | FAR-100/MC-CDU-1-A01 | TB04-3/4 | JB-DA-C2-1 | 7/8 | MC-DA-C2-1 | 4 | 100 | C2 | H-101 |  |  | 0-100000 | kg/h | instrument index
FT-1013 | FT-1013 | Flow transmitter | H-101 pass 3 flow | FIC-1013 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 3 | FAR-100/MC-CDU-1-A01 | TB04-5/6 | JB-DA-C2-1 | 9/10 | MC-DA-C2-1 | 5 | 100 | C2 | H-101 |  |  | 0-100000 | kg/h | instrument index
FT-1014 | FT-1014 | Flow transmitter | H-101 pass 4 flow | FIC-1014 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 4 | FAR-100/MC-CDU-1-A01 | TB04-7/8 | JB-DA-C2-1 | 11/12 | MC-DA-C2-1 | 6 | 100 | C2 | H-101 |  |  | 0-100000 | kg/h | instrument index
FT-1015 | FT-1015 | Flow transmitter | H-101 pass 5 flow | FIC-1015 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 5 | FAR-100/MC-CDU-1-A01 | TB04-9/10 | JB-DA-C2-1 | 13/14 | MC-DA-C2-1 | 7 | 100 | C2 | H-101 |  |  | 0-100000 | kg/h | instrument index
FT-1016 | FT-1016 | Flow transmitter | H-101 pass 6 flow | FIC-1016 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 6 | FAR-100/MC-CDU-1-A01 | TB04-11/12 | JB-DA-C2-1 | 15/16 | MC-DA-C2-1 | 8 | 100 | C2 | H-101 |  |  | 0-100000 | kg/h | instrument index
FT-1017 | FT-1017 | Flow transmitter | H-101 pass 7 flow | FIC-1017 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 7 | FAR-100/MC-CDU-1-A01 | TB04-13/14 | JB-DA-C2-1 | 17/18 | MC-DA-C2-1 | 9 | 100 | C2 | H-101 |  |  | 0-100000 | kg/h | instrument index
FT-1018 | FT-1018 | Flow transmitter | H-101 pass 8 flow | FIC-1018 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 8 | FAR-100/MC-CDU-1-A01 | TB04-15/16 | JB-DA-C2-1 | 19/20 | MC-DA-C2-1 | 10 | 100 | C2 | H-101 |  |  | 0-100000 | kg/h | instrument index
FT-1021 | FT-1021 | Flow transmitter | H-101 fuel gas flow (fuel/air cross-limiting) | PIC-1021 | CFU-100-PR-PID-005 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 9 | FAR-100/MC-CDU-1-A01 | TB04-17/18 | JB-DA-C2-1 | 21/22 | MC-DA-C2-1 | 11 | 100 | C2 | H-101 |  |  | 0-8000 | kg/h | instrument index
FT-1021 | FT-1021 | Flow transmitter | H-101 fuel gas flow (cross-limiting fuel measurement) | FT-1021 | (P&ID sheet 005) | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 10 | FAR-100/MC-CDU-1-A01 | TB04-19/20 | JB-DA-C2-1 | 23/24 | MC-DA-C2-1 | 12 | 100 | C2 | H-101 |  |  |  |  | I&C addition (add to index)
FT-1025 | FT-1025 | Flow transmitter | H-101 combustion air flow | FIC-1025 | CFU-100-PR-PID-005 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 11 | FAR-100/MC-CDU-1-A01 | TB04-21/22 | JB-DA-C2-1 | 25/26 | MC-DA-C2-1 | 13 | 100 | C2 | H-101 |  |  | 0-100 | % | instrument index
PI-1224 | PI-1224 | Pressure gauge | Crude to H-101 pressure | PI-1224 | CFU-100-PR-PID-003 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 12 | FAR-100/MC-CDU-1-A01 | TB04-23/24 | JB-DA-C2-1 | 45/46 | MC-DA-C2-1 | 23 | 100 | C2 | H-101 |  |  | 0-30 | barg | instrument index
PI-1227 | PI-1227 | Pressure gauge | Stripping steam pressure | PI-1227 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI04 | 13 | FAR-100/MC-CDU-1-A01 | TB04-25/26 | JB-DA-C2-1 | 47/48 | MC-DA-C2-1 | 24 | 100 | C2 | H-101 |  |  | 0-6 | barg | instrument index
PT-1021 | PT-1021 | Pressure transmitter | H-101 fuel gas burner pressure | PIC-1021 | CFU-100-PR-PID-005 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 1 | FAR-100/MC-CDU-1-A01 | TB05-1/2 | JB-DA-C2-2 | 1/2 | MC-DA-C2-2 | 1 | 100 | C2 | H-101 |  |  | 0-4 | barg | instrument index
PT-1023 | PT-1023 | Pressure transmitter | H-101 arch draft | PIC-1023 | CFU-100-PR-PID-005 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 2 | FAR-100/MC-CDU-1-A01 | TB05-3/4 | JB-DA-C2-2 | 3/4 | MC-DA-C2-2 | 2 | 100 | C2 | H-101 |  |  | -25-25 | mmH2O | instrument index
TI-1011 | TI-1011 | Temperature indicator | H-101 pass 1 outlet temperature | FIC-1011 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 3 | FAR-100/MC-CDU-1-A01 | TB05-5/6 | JB-DA-C2-2 | 11/12 | MC-DA-C2-2 | 6 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
TI-1012 | TI-1012 | Temperature indicator | H-101 pass 2 outlet temperature | FIC-1012 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 4 | FAR-100/MC-CDU-1-A01 | TB05-7/8 | JB-DA-C2-2 | 13/14 | MC-DA-C2-2 | 7 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
TI-1013 | TI-1013 | Temperature indicator | H-101 pass 3 outlet temperature | FIC-1013 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 5 | FAR-100/MC-CDU-1-A01 | TB05-9/10 | JB-DA-C2-2 | 15/16 | MC-DA-C2-2 | 8 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
TI-1014 | TI-1014 | Temperature indicator | H-101 pass 4 outlet temperature | FIC-1014 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 6 | FAR-100/MC-CDU-1-A01 | TB05-11/12 | JB-DA-C2-2 | 17/18 | MC-DA-C2-2 | 9 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
TI-1015 | TI-1015 | Temperature indicator | H-101 pass 5 outlet temperature | FIC-1015 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 7 | FAR-100/MC-CDU-1-A01 | TB05-13/14 | JB-DA-C2-2 | 19/20 | MC-DA-C2-2 | 10 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
TI-1016 | TI-1016 | Temperature indicator | H-101 pass 6 outlet temperature | FIC-1016 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 8 | FAR-100/MC-CDU-1-A01 | TB05-15/16 | JB-DA-C2-2 | 21/22 | MC-DA-C2-2 | 11 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
TI-1017 | TI-1017 | Temperature indicator | H-101 pass 7 outlet temperature | FIC-1017 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 9 | FAR-100/MC-CDU-1-A01 | TB05-17/18 | JB-DA-C2-2 | 23/24 | MC-DA-C2-2 | 12 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
TI-1018 | TI-1018 | Temperature indicator | H-101 pass 8 outlet temperature | FIC-1018 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 10 | FAR-100/MC-CDU-1-A01 | TB05-19/20 | JB-DA-C2-2 | 25/26 | MC-DA-C2-2 | 13 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
TI-1226 | TI-1226 | Temperature indicator | H-101 inlet temperature (CIT) | TI-1226 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 11 | FAR-100/MC-CDU-1-A01 | TB05-21/22 | JB-DA-C2-2 | 27/28 | MC-DA-C2-2 | 14 | 100 | C2 | H-101 |  |  | 0-400 | C | instrument index
TI-1228 | TI-1228 | Temperature indicator | H-101 flue gas temperature (bridgewall) | TI-1228 | CFU-100-PR-PID-005 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 12 | FAR-100/MC-CDU-1-A01 | TB05-23/24 | JB-DA-C2-2 | 29/30 | MC-DA-C2-2 | 15 | 100 | C2 | H-101 |  |  | 0-400 | C | instrument index
TT-1020 | TT-1020 | Temperature transmitter | H-101 coil outlet temperature (COT) | TIC-1020 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI05 | 13 | FAR-100/MC-CDU-1-A01 | TB05-25/26 | JB-DA-C2-2 | 31/32 | MC-DA-C2-2 | 16 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
TT-1024 | TT-1024 | Temperature transmitter | Stripping-steam superheat outlet | TIC-1024 | CFU-100-PR-PID-004 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI06 | 1 | FAR-100/MC-CDU-1-A01 | TB06-1/2 | JB-DA-C2-2 | 33/34 | MC-DA-C2-2 | 17 | 100 | C2 | H-101 |  |  | 0-500 | C | instrument index
AT-1021 | AT-1021 | Analyser transmitter | Fuel gas Wobbe index / LHV (calorimeter) | AT-1021 | (P&ID sheet 016) | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI06 | 2 | FAR-100/MC-CDU-1-A01 | TB06-3/4 | JB-DA-D1 | 1/2 | MC-DA-D1 | 1 | 140 | D1 | D-103 |  |  |  |  | I&C addition (add to index)
LT-9002 | LT-9002 | Level transmitter | D-103 liquid level | LIC-9002 | CFU-900-PR-PID-016 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI06 | 3 | FAR-100/MC-CDU-1-A01 | TB06-5/6 | JB-DA-D1 | 3/4 | MC-DA-D1 | 2 | 140 | D1 | D-103 |  |  | 0-100 | % | instrument index
PT-9001 | PT-9001 | Pressure transmitter | Fuel gas header pressure | PIC-9001 | CFU-900-PR-PID-016 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI06 | 4 | FAR-100/MC-CDU-1-A01 | TB06-7/8 | JB-DA-D1 | 7/8 | MC-DA-D1 | 4 | 140 | D1 | D-103 |  |  | 0-6 | barg | instrument index
PT-9004 | PT-9004 | Pressure transmitter | LP steam header pressure (unit) | PIC-9004 | CFU-900-PR-PID-016 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI06 | 5 | FAR-100/MC-CDU-1-A01 | TB06-9/10 | JB-DA-D1 | 9/10 | MC-DA-D1 | 5 | 140 | D1 | D-103 |  |  | 0-6 | barg | instrument index
TT-9005 | TT-9005 | Temperature transmitter | Ambient air temperature (APC DV, air coolers) | TT-9005 | CFU-900-PR-PID-016 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI06 | 6 | FAR-100/MC-CDU-1-A01 | TB06-11/12 | JB-DA-D1 | 15/16 | MC-DA-D1 | 8 | 140 | D1 | D-103 |  |  | -20-60 | C | instrument index
LT-9003 | LT-9003 | Level transmitter | D-104 flare KO drum level | LIC-9003 | CFU-900-PR-PID-016 | DCS | CDU-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-1-AI06 | 7 | FAR-100/MC-CDU-1-A01 | TB06-13/14 | JB-DA-D5 | 1/2 | MC-DA-D5 | 1 | 260 | D5 | D-104 |  |  | 0-100 | % | instrument index
LV-1007 | LV-1007 | Level control valve | D-101A water/oil interface - Valve positioner / output | LIC-1007 | CFU-100-PR-PID-002 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO01 | 1 | FAR-100/MC-CDU-1-A01 | TB01-1/2 | JB-DA-A2 | 17/18 | MC-DA-A2 | 9 | 90 | A2 | D-101A |  |  |  |  | instrument index
LV-1008 | LV-1008 | Level control valve | D-101B water/oil interface - Valve positioner / output | LIC-1008 | CFU-100-PR-PID-002 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO01 | 2 | FAR-100/MC-CDU-1-A01 | TB01-3/4 | JB-DA-A2 | 19/20 | MC-DA-A2 | 10 | 80 | A2 | D-101B |  |  |  |  | instrument index
PDV-1005 | PDV-1005 | Differential pressure control (mix) valve | 1st-stage mix valve dP - Valve positioner / output | PDIC-1005 | CFU-100-PR-PID-002 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO01 | 3 | FAR-100/MC-CDU-1-A01 | TB01-5/6 | JB-DA-A2 | 25/26 | MC-DA-A2 | 13 | 90 | A2 | D-101A |  |  |  |  | instrument index
PDV-1006 | PDV-1006 | Differential pressure control (mix) valve | 2nd-stage mix valve dP - Valve positioner / output | PDIC-1006 | CFU-100-PR-PID-002 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO01 | 4 | FAR-100/MC-CDU-1-A01 | TB01-7/8 | JB-DA-A2 | 27/28 | MC-DA-A2 | 14 | 80 | A2 | D-101B |  |  |  |  | instrument index
PV-1009 | PV-1009 | Pressure control valve | Desalter pressure (above crude vapour pressure) - Valve positioner / output | PIC-1009 | CFU-100-PR-PID-002 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO01 | 5 | FAR-100/MC-CDU-1-A01 | TB01-9/10 | JB-DA-A2 | 35/36 | MC-DA-A2 | 18 | 80 | A2 | D-101B |  |  |  |  | instrument index
TV-1004 | TV-1004 | Temperature control valve | Desalter inlet temperature - Valve positioner / output | TIC-1004 | CFU-100-PR-PID-001 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO01 | 6 | FAR-100/MC-CDU-1-A01 | TB01-11/12 | JB-DA-A2 | 45/46 | MC-DA-A2 | 23 | 90 | A2 | D-101A |  |  |  |  | instrument index
FV-1001 | FV-1001 | Flow control valve | Crude charge flow (unit throughput) - Valve positioner / output | FIC-1001 | CFU-100-PR-PID-001 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO02 | 1 | FAR-100/MC-CDU-1-A01 | TB02-1/2 | JB-DA-A3 | 9/10 | MC-DA-A3 | 5 | 160 | A3 | P-101A |  |  |  |  | instrument index
FV-1003 | FV-1003 | Flow control valve | Wash water ratio to crude (5 LV%) - Valve positioner / output | FFIC-1003 | CFU-100-PR-PID-002 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO02 | 2 | FAR-100/MC-CDU-1-A01 | TB02-3/4 | JB-DA-A3 | 11/12 | MC-DA-A3 | 6 | 120 | A3 | P-114A |  |  |  |  | instrument index
TV-1041 | TV-1041 | Temperature control valve | TPA return temperature (duty) - Valve positioner / output | TIC-1041 | CFU-100-PR-PID-001 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO02 | 3 | FAR-100/MC-CDU-1-A01 | TB02-5/6 | JB-DA-A3 | 15/16 | MC-DA-A3 | 8 | 160 | A3 | P-101A |  |  |  |  | instrument index
TV-1043 | TV-1043 | Temperature control valve | MPA return temperature - Valve positioner / output | TIC-1043 | CFU-100-PR-PID-003 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO02 | 4 | FAR-100/MC-CDU-1-A01 | TB02-7/8 | JB-DA-A4 | 25/26 | MC-DA-A4 | 13 | 160 | A4 | E-108A |  |  |  |  | instrument index
TV-1045 | TV-1045 | Temperature control valve | BPA return temperature - Valve positioner / output | TIC-1045 | CFU-100-PR-PID-003 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO02 | 5 | FAR-100/MC-CDU-1-A01 | TB02-9/10 | JB-DA-A4 | 27/28 | MC-DA-A4 | 14 | 160 | A4 | E-108A |  |  |  |  | instrument index
TV-2017 | TV-2017 | Temperature control valve | HVGO PA return temperature - Valve positioner / output | TIC-2017 | CFU-100-PR-PID-003, CFU-200-PR-PID-014 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO02 | 6 | FAR-100/MC-CDU-1-A01 | TB02-11/12 | JB-DA-A4 | 29/30 | MC-DA-A4 | 15 | 160 | A4 | E-108A |  |  |  |  | instrument index
FY-1002 | FY-1002 | Flow relay / computing block | Demulsifier pump stroke positioner - Valve positioner / output | FFIC-1002 | CFU-100-PR-PID-001 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO03 | 1 | FAR-100/MC-CDU-1-A01 | TB03-1/2 | JB-DA-B2 | 1/2 | MC-DA-B2 | 1 | 80 | B2 | X-101 |  |  |  |  | instrument index
LV-1110 | LV-1110 | Level control valve | E-113 steam-generator level - Valve positioner / output | LIC-1110 | CFU-100-PR-PID-003 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO03 | 2 | FAR-100/MC-CDU-1-A01 | TB03-3/4 | JB-DA-B4-2 | 15/16 | MC-DA-B4-2 | 8 | 160 | B4 | E-113 |  |  |  |  | instrument index
PV-1111 | PV-1111 | Pressure control valve | E-113 MP steam pressure - Valve positioner / output | PIC-1111 | CFU-100-PR-PID-003 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO03 | 3 | FAR-100/MC-CDU-1-A01 | TB03-5/6 | JB-DA-B4-2 | 35/36 | MC-DA-B4-2 | 18 | 160 | B4 | E-113 |  |  |  |  | instrument index
FV-1011 | FV-1011 | Flow control valve | H-101 pass 1 flow - Valve positioner / output | FIC-1011 | CFU-100-PR-PID-004 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO03 | 4 | FAR-100/MC-CDU-1-A01 | TB03-7/8 | JB-DA-C2-1 | 27/28 | MC-DA-C2-1 | 14 | 100 | C2 | H-101 |  |  |  |  | instrument index
FV-1012 | FV-1012 | Flow control valve | H-101 pass 2 flow - Valve positioner / output | FIC-1012 | CFU-100-PR-PID-004 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO03 | 5 | FAR-100/MC-CDU-1-A01 | TB03-9/10 | JB-DA-C2-1 | 29/30 | MC-DA-C2-1 | 15 | 100 | C2 | H-101 |  |  |  |  | instrument index
FV-1013 | FV-1013 | Flow control valve | H-101 pass 3 flow - Valve positioner / output | FIC-1013 | CFU-100-PR-PID-004 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO03 | 6 | FAR-100/MC-CDU-1-A01 | TB03-11/12 | JB-DA-C2-1 | 31/32 | MC-DA-C2-1 | 16 | 100 | C2 | H-101 |  |  |  |  | instrument index
FV-1014 | FV-1014 | Flow control valve | H-101 pass 4 flow - Valve positioner / output | FIC-1014 | CFU-100-PR-PID-004 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO04 | 1 | FAR-100/MC-CDU-1-A01 | TB04-1/2 | JB-DA-C2-1 | 33/34 | MC-DA-C2-1 | 17 | 100 | C2 | H-101 |  |  |  |  | instrument index
FV-1015 | FV-1015 | Flow control valve | H-101 pass 5 flow - Valve positioner / output | FIC-1015 | CFU-100-PR-PID-004 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO04 | 2 | FAR-100/MC-CDU-1-A01 | TB04-3/4 | JB-DA-C2-1 | 35/36 | MC-DA-C2-1 | 18 | 100 | C2 | H-101 |  |  |  |  | instrument index
FV-1016 | FV-1016 | Flow control valve | H-101 pass 6 flow - Valve positioner / output | FIC-1016 | CFU-100-PR-PID-004 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO04 | 3 | FAR-100/MC-CDU-1-A01 | TB04-5/6 | JB-DA-C2-1 | 37/38 | MC-DA-C2-1 | 19 | 100 | C2 | H-101 |  |  |  |  | instrument index
FV-1017 | FV-1017 | Flow control valve | H-101 pass 7 flow - Valve positioner / output | FIC-1017 | CFU-100-PR-PID-004 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO04 | 4 | FAR-100/MC-CDU-1-A01 | TB04-7/8 | JB-DA-C2-1 | 39/40 | MC-DA-C2-1 | 20 | 100 | C2 | H-101 |  |  |  |  | instrument index
FV-1018 | FV-1018 | Flow control valve | H-101 pass 8 flow - Valve positioner / output | FIC-1018 | CFU-100-PR-PID-004 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO04 | 5 | FAR-100/MC-CDU-1-A01 | TB04-9/10 | JB-DA-C2-1 | 41/42 | MC-DA-C2-1 | 21 | 100 | C2 | H-101 |  |  |  |  | instrument index
FV-1025 | FV-1025 | Flow control valve | H-101 FD fan inlet vanes (FIC-1025) - Valve positioner / output | FIC-1025 | CFU-100-PR-PID-005 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO04 | 6 | FAR-100/MC-CDU-1-A01 | TB04-11/12 | JB-DA-C2-1 | 43/44 | MC-DA-C2-1 | 22 | 100 | C2 | H-101 |  |  |  |  | instrument index
PV-1021 | PV-1021 | Pressure control valve | H-101 fuel gas burner pressure - Valve positioner / output | PIC-1021 | CFU-100-PR-PID-005 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO05 | 1 | FAR-100/MC-CDU-1-A01 | TB05-1/2 | JB-DA-C2-2 | 5/6 | MC-DA-C2-2 | 3 | 100 | C2 | H-101 |  |  |  |  | instrument index
PV-1023 | PV-1023 | Pressure control valve | H-101 stack damper actuator - Valve positioner / output | PIC-1023 | CFU-100-PR-PID-005 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO05 | 2 | FAR-100/MC-CDU-1-A01 | TB05-3/4 | JB-DA-C2-2 | 7/8 | MC-DA-C2-2 | 4 | 100 | C2 | H-101 |  |  |  |  | instrument index
PY-1023 | PY-1023 | Pressure relay / VSD signal | ID fan VSD speed signal / stack damper - Valve positioner / output | PIC-1023 | CFU-100-PR-PID-005 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO05 | 3 | FAR-100/MC-CDU-1-A01 | TB05-5/6 | JB-DA-C2-2 | 9/10 | MC-DA-C2-2 | 5 | 100 | C2 | H-101 |  |  |  |  | instrument index
TV-1024 | TV-1024 | Temperature control valve | Stripping-steam superheat outlet - Valve positioner / output | TIC-1024 | CFU-100-PR-PID-004 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO05 | 4 | FAR-100/MC-CDU-1-A01 | TB05-7/8 | JB-DA-C2-2 | 35/36 | MC-DA-C2-2 | 18 | 100 | C2 | H-101 |  |  |  |  | instrument index
LV-9002 | LV-9002 | Level control valve | D-103 liquid level - Valve positioner / output | LIC-9002 | CFU-900-PR-PID-016 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO05 | 5 | FAR-100/MC-CDU-1-A01 | TB05-9/10 | JB-DA-D1 | 5/6 | MC-DA-D1 | 3 | 140 | D1 | D-103 |  |  |  |  | instrument index
PV-9001 | PV-9001 | Pressure control valve | Fuel gas header pressure - Valve positioner / output | PIC-9001 | CFU-900-PR-PID-016 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO05 | 6 | FAR-100/MC-CDU-1-A01 | TB05-11/12 | JB-DA-D1 | 11/12 | MC-DA-D1 | 6 | 140 | D1 | D-103 |  |  |  |  | instrument index
PV-9004 | PV-9004 | Pressure control valve | LP steam header pressure (unit) - Valve positioner / output | PIC-9004 | CFU-900-PR-PID-016 | DCS | CDU-1 | AO | 4-20 mA HART to smart positioner | CDU-1-AO06 | 1 | FAR-100/MC-CDU-1-A01 | TB06-1/2 | JB-DA-D1 | 13/14 | MC-DA-D1 | 7 | 140 | D1 | D-103 |  |  |  |  | instrument index
P-101A XA | P-101A | Motor interface (MCC) | Crude charge P-101A - Motor fault / not available (710 kW) | P-101A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 1 | FAR-100/MC-CDU-1-D01 | TB01-1/2 | JB-DD-A3 | 5/6 | MC-DD-A3 | 3 | 160 | A3 | P-101A |  |  |  |  | equipment.json (MCC hardwired interface)
P-101A XL | P-101A | Motor interface (MCC) | Crude charge P-101A - Motor running (710 kW) | P-101A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 2 | FAR-100/MC-CDU-1-D01 | TB01-3/4 | JB-DD-A3 | 7/8 | MC-DD-A3 | 4 | 160 | A3 | P-101A |  |  |  |  | equipment.json (MCC hardwired interface)
P-101B XA | P-101B | Motor interface (MCC) | Crude charge P-101B - Motor fault / not available (710 kW) | P-101B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 3 | FAR-100/MC-CDU-1-D01 | TB01-5/6 | JB-DD-A3 | 13/14 | MC-DD-A3 | 7 | 150 | A3 | P-101B |  |  |  |  | equipment.json (MCC hardwired interface)
P-101B XL | P-101B | Motor interface (MCC) | Crude charge P-101B - Motor running (710 kW) | P-101B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 4 | FAR-100/MC-CDU-1-D01 | TB01-7/8 | JB-DD-A3 | 15/16 | MC-DD-A3 | 8 | 150 | A3 | P-101B |  |  |  |  | equipment.json (MCC hardwired interface)
P-114A XA | P-114A | Motor interface (MCC) | Desalter wash water P-114A - Motor fault / not available (30 kW) | P-114A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 5 | FAR-100/MC-CDU-1-D01 | TB01-9/10 | JB-DD-A3 | 21/22 | MC-DD-A3 | 11 | 120 | A3 | P-114A |  |  |  |  | equipment.json (MCC hardwired interface)
P-114A XL | P-114A | Motor interface (MCC) | Desalter wash water P-114A - Motor running (30 kW) | P-114A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 6 | FAR-100/MC-CDU-1-D01 | TB01-11/12 | JB-DD-A3 | 23/24 | MC-DD-A3 | 12 | 120 | A3 | P-114A |  |  |  |  | equipment.json (MCC hardwired interface)
P-114B XA | P-114B | Motor interface (MCC) | Desalter wash water P-114B - Motor fault / not available (30 kW) | P-114B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 7 | FAR-100/MC-CDU-1-D01 | TB01-13/14 | JB-DD-A3 | 29/30 | MC-DD-A3 | 15 | 120 | A3 | P-114B |  |  |  |  | equipment.json (MCC hardwired interface)
P-114B XL | P-114B | Motor interface (MCC) | Desalter wash water P-114B - Motor running (30 kW) | P-114B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 8 | FAR-100/MC-CDU-1-D01 | TB01-15/16 | JB-DD-A3 | 31/32 | MC-DD-A3 | 16 | 120 | A3 | P-114B |  |  |  |  | equipment.json (MCC hardwired interface)
P-118 XA | P-118 | Motor interface (MCC) | Desalter mud-wash / recycle P-118 - Motor fault / not available (7.5 kW) | P-118 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 9 | FAR-100/MC-CDU-1-D01 | TB01-17/18 | JB-DD-A3 | 37/38 | MC-DD-A3 | 19 | 110 | A3 | P-118 |  |  |  |  | equipment.json (MCC hardwired interface)
P-118 XL | P-118 | Motor interface (MCC) | Desalter mud-wash / recycle P-118 - Motor running (7.5 kW) | P-118 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 10 | FAR-100/MC-CDU-1-D01 | TB01-19/20 | JB-DD-A3 | 39/40 | MC-DD-A3 | 20 | 110 | A3 | P-118 |  |  |  |  | equipment.json (MCC hardwired interface)
X-101 XA | X-101 | Motor interface (MCC) | Demulsifier injection package X-101 - Motor fault / not available (0.75 kW) | X-101 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 11 | FAR-100/MC-CDU-1-D01 | TB01-21/22 | JB-DD-B2 | 5/6 | MC-DD-B2 | 3 | 80 | B2 | X-101 |  |  |  |  | equipment.json (MCC hardwired interface)
X-101 XL | X-101 | Motor interface (MCC) | Demulsifier injection package X-101 - Motor running (0.75 kW) | X-101 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 12 | FAR-100/MC-CDU-1-D01 | TB01-23/24 | JB-DD-B2 | 7/8 | MC-DD-B2 | 4 | 80 | B2 | X-101 |  |  |  |  | equipment.json (MCC hardwired interface)
X-102 XA | X-102 | Motor interface (MCC) | Caustic injection package (desalted crude) X-102 - Motor fault / not available (0.75 kW) | X-102 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 13 | FAR-100/MC-CDU-1-D01 | TB01-25/26 | JB-DD-B2 | 13/14 | MC-DD-B2 | 7 | 80 | B2 | X-102 |  |  |  |  | equipment.json (MCC hardwired interface)
X-102 XL | X-102 | Motor interface (MCC) | Caustic injection package (desalted crude) X-102 - Motor running (0.75 kW) | X-102 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 14 | FAR-100/MC-CDU-1-D01 | TB01-27/28 | JB-DD-B2 | 15/16 | MC-DD-B2 | 8 | 80 | B2 | X-102 |  |  |  |  | equipment.json (MCC hardwired interface)
P-102A XA | P-102A | Motor interface (MCC) | Desalted crude booster P-102A - Motor fault / not available (710 kW) | P-102A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 15 | FAR-100/MC-CDU-1-D01 | TB01-29/30 | JB-DD-B3-1 | 21/22 | MC-DD-B3-1 | 11 | 100 | B3 | P-102A |  |  |  |  | equipment.json (MCC hardwired interface)
P-102A XL | P-102A | Motor interface (MCC) | Desalted crude booster P-102A - Motor running (710 kW) | P-102A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 16 | FAR-100/MC-CDU-1-D01 | TB01-31/32 | JB-DD-B3-1 | 23/24 | MC-DD-B3-1 | 12 | 100 | B3 | P-102A |  |  |  |  | equipment.json (MCC hardwired interface)
P-102B XA | P-102B | Motor interface (MCC) | Desalted crude booster P-102B - Motor fault / not available (710 kW) | P-102B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 17 | FAR-100/MC-CDU-1-D01 | TB01-33/34 | JB-DD-B3-1 | 29/30 | MC-DD-B3-1 | 15 | 90 | B3 | P-102B |  |  |  |  | equipment.json (MCC hardwired interface)
P-102B XL | P-102B | Motor interface (MCC) | Desalted crude booster P-102B - Motor running (710 kW) | P-102B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 18 | FAR-100/MC-CDU-1-D01 | TB01-35/36 | JB-DD-B3-1 | 31/32 | MC-DD-B3-1 | 16 | 90 | B3 | P-102B |  |  |  |  | equipment.json (MCC hardwired interface)
X-103 XA | X-103 | Motor interface (MCC) | Neutraliser / filming amine package (atm OH) X-103 - Motor fault / not available (0.75 kW) | X-103 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 19 | FAR-100/MC-CDU-1-D01 | TB01-37/38 | JB-DD-B4 | 5/6 | MC-DD-B4 | 3 | 160 | B4 | X-103 |  |  |  |  | equipment.json (MCC hardwired interface)
X-103 XL | X-103 | Motor interface (MCC) | Neutraliser / filming amine package (atm OH) X-103 - Motor running (0.75 kW) | X-103 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 20 | FAR-100/MC-CDU-1-D01 | TB01-39/40 | JB-DD-B4 | 7/8 | MC-DD-B4 | 4 | 160 | B4 | X-103 |  |  |  |  | equipment.json (MCC hardwired interface)
K-101A XA | K-101A | Motor interface (MCC) | H-101 forced-draft fan K-101A - Motor fault / not available (90 kW) | K-101A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 21 | FAR-100/MC-CDU-1-D01 | TB01-41/42 | JB-DD-C1 | 5/6 | MC-DD-C1 | 3 | 90 | C1 | K-101A |  |  |  |  | equipment.json (MCC hardwired interface)
K-101A XL | K-101A | Motor interface (MCC) | H-101 forced-draft fan K-101A - Motor running (90 kW) | K-101A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 22 | FAR-100/MC-CDU-1-D01 | TB01-43/44 | JB-DD-C1 | 7/8 | MC-DD-C1 | 4 | 90 | C1 | K-101A |  |  |  |  | equipment.json (MCC hardwired interface)
K-101B XA | K-101B | Motor interface (MCC) | H-101 forced-draft fan K-101B - Motor fault / not available (90 kW) | K-101B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 23 | FAR-100/MC-CDU-1-D01 | TB01-45/46 | JB-DD-C1 | 13/14 | MC-DD-C1 | 7 | 90 | C1 | K-101B |  |  |  |  | equipment.json (MCC hardwired interface)
K-101B XL | K-101B | Motor interface (MCC) | H-101 forced-draft fan K-101B - Motor running (90 kW) | K-101B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 24 | FAR-100/MC-CDU-1-D01 | TB01-47/48 | JB-DD-C1 | 15/16 | MC-DD-C1 | 8 | 90 | C1 | K-101B |  |  |  |  | equipment.json (MCC hardwired interface)
K-102A XA | K-102A | Motor interface (MCC) | H-101 induced-draft fan K-102A - Motor fault / not available (200 kW) | K-102A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 25 | FAR-100/MC-CDU-1-D01 | TB01-49/50 | JB-DD-C1 | 21/22 | MC-DD-C1 | 11 | 100 | C1 | K-102A |  |  |  |  | equipment.json (MCC hardwired interface)
K-102A XL | K-102A | Motor interface (MCC) | H-101 induced-draft fan K-102A - Motor running (200 kW) | K-102A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI01 | 26 | FAR-100/MC-CDU-1-D01 | TB01-51/52 | JB-DD-C1 | 23/24 | MC-DD-C1 | 12 | 100 | C1 | K-102A |  |  |  |  | equipment.json (MCC hardwired interface)
K-102B XA | K-102B | Motor interface (MCC) | H-101 induced-draft fan K-102B - Motor fault / not available (200 kW) | K-102B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI02 | 1 | FAR-100/MC-CDU-1-D01 | TB02-1/2 | JB-DD-C1 | 29/30 | MC-DD-C1 | 15 | 100 | C1 | K-102B |  |  |  |  | equipment.json (MCC hardwired interface)
K-102B XL | K-102B | Motor interface (MCC) | H-101 induced-draft fan K-102B - Motor running (200 kW) | K-102B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI02 | 2 | FAR-100/MC-CDU-1-D01 | TB02-3/4 | JB-DD-C1 | 31/32 | MC-DD-C1 | 16 | 100 | C1 | K-102B |  |  |  |  | equipment.json (MCC hardwired interface)
XA-9101 | XA-9101 | Common alarm (analyser house) | Analyser house AH-101 common trouble / HVAC alarm | XA-9101 | CFU-900-PR-PID-016 | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI02 | 3 | FAR-100/MC-CDU-1-D01 | TB02-5/6 | JB-DD-D1 | 1/2 | MC-DD-D1 | 1 | 140 | D1 | D-103 |  |  | Alarm | - | instrument index
P-119A XA | P-119A | Motor interface (MCC) | Flare KO drum pump-out P-119A - Motor fault / not available (7.5 kW) | P-119A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI02 | 4 | FAR-100/MC-CDU-1-D01 | TB02-7/8 | JB-DD-D5 | 7/8 | MC-DD-D5 | 4 | 250 | D5 | P-119A |  |  |  |  | equipment.json (MCC hardwired interface)
P-119A XL | P-119A | Motor interface (MCC) | Flare KO drum pump-out P-119A - Motor running (7.5 kW) | P-119A |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI02 | 5 | FAR-100/MC-CDU-1-D01 | TB02-9/10 | JB-DD-D5 | 9/10 | MC-DD-D5 | 5 | 250 | D5 | P-119A |  |  |  |  | equipment.json (MCC hardwired interface)
P-119B XA | P-119B | Motor interface (MCC) | Flare KO drum pump-out P-119B - Motor fault / not available (7.5 kW) | P-119B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI02 | 6 | FAR-100/MC-CDU-1-D01 | TB02-11/12 | JB-DD-D5 | 15/16 | MC-DD-D5 | 8 | 250 | D5 | P-119B |  |  |  |  | equipment.json (MCC hardwired interface)
P-119B XL | P-119B | Motor interface (MCC) | Flare KO drum pump-out P-119B - Motor running (7.5 kW) | P-119B |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI02 | 7 | FAR-100/MC-CDU-1-D01 | TB02-13/14 | JB-DD-D5 | 17/18 | MC-DD-D5 | 9 | 250 | D5 | P-119B |  |  |  |  | equipment.json (MCC hardwired interface)
X-104 XA | X-104 | Motor interface (MCC) | Corrosion inhibitor package (VDU OH) X-104 - Motor fault / not available (0.75 kW) | X-104 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI02 | 8 | FAR-100/MC-CDU-1-D01 | TB02-15/16 | JB-DD-F4 | 13/14 | MC-DD-F4 | 7 | 320 | F4 | X-104 |  |  |  |  | equipment.json (MCC hardwired interface)
X-104 XL | X-104 | Motor interface (MCC) | Corrosion inhibitor package (VDU OH) X-104 - Motor running (0.75 kW) | X-104 |  | DCS | CDU-1 | DI | 24 VDC dry contact / NAMUR | CDU-1-DI02 | 9 | FAR-100/MC-CDU-1-D01 | TB02-17/18 | JB-DD-F4 | 15/16 | MC-DD-F4 | 8 | 320 | F4 | X-104 |  |  |  |  | equipment.json (MCC hardwired interface)
P-101A HS-START | P-101A | Motor interface (MCC) | Crude charge P-101A - Start command (710 kW) | P-101A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 1 | FAR-100/MC-CDU-1-D01 | TB01-1/2 | JB-DD-A3 | 1/2 | MC-DD-A3 | 1 | 160 | A3 | P-101A |  |  |  |  | equipment.json (MCC hardwired interface)
P-101A HS-STOP | P-101A | Motor interface (MCC) | Crude charge P-101A - Stop command (710 kW) | P-101A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 2 | FAR-100/MC-CDU-1-D01 | TB01-3/4 | JB-DD-A3 | 3/4 | MC-DD-A3 | 2 | 160 | A3 | P-101A |  |  |  |  | equipment.json (MCC hardwired interface)
P-101B HS-START | P-101B | Motor interface (MCC) | Crude charge P-101B - Start command (710 kW) | P-101B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 3 | FAR-100/MC-CDU-1-D01 | TB01-5/6 | JB-DD-A3 | 9/10 | MC-DD-A3 | 5 | 150 | A3 | P-101B |  |  |  |  | equipment.json (MCC hardwired interface)
P-101B HS-STOP | P-101B | Motor interface (MCC) | Crude charge P-101B - Stop command (710 kW) | P-101B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 4 | FAR-100/MC-CDU-1-D01 | TB01-7/8 | JB-DD-A3 | 11/12 | MC-DD-A3 | 6 | 150 | A3 | P-101B |  |  |  |  | equipment.json (MCC hardwired interface)
P-114A HS-START | P-114A | Motor interface (MCC) | Desalter wash water P-114A - Start command (30 kW) | P-114A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 5 | FAR-100/MC-CDU-1-D01 | TB01-9/10 | JB-DD-A3 | 17/18 | MC-DD-A3 | 9 | 120 | A3 | P-114A |  |  |  |  | equipment.json (MCC hardwired interface)
P-114A HS-STOP | P-114A | Motor interface (MCC) | Desalter wash water P-114A - Stop command (30 kW) | P-114A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 6 | FAR-100/MC-CDU-1-D01 | TB01-11/12 | JB-DD-A3 | 19/20 | MC-DD-A3 | 10 | 120 | A3 | P-114A |  |  |  |  | equipment.json (MCC hardwired interface)
P-114B HS-START | P-114B | Motor interface (MCC) | Desalter wash water P-114B - Start command (30 kW) | P-114B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 7 | FAR-100/MC-CDU-1-D01 | TB01-13/14 | JB-DD-A3 | 25/26 | MC-DD-A3 | 13 | 120 | A3 | P-114B |  |  |  |  | equipment.json (MCC hardwired interface)
P-114B HS-STOP | P-114B | Motor interface (MCC) | Desalter wash water P-114B - Stop command (30 kW) | P-114B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 8 | FAR-100/MC-CDU-1-D01 | TB01-15/16 | JB-DD-A3 | 27/28 | MC-DD-A3 | 14 | 120 | A3 | P-114B |  |  |  |  | equipment.json (MCC hardwired interface)
P-118 HS-START | P-118 | Motor interface (MCC) | Desalter mud-wash / recycle P-118 - Start command (7.5 kW) | P-118 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 9 | FAR-100/MC-CDU-1-D01 | TB01-17/18 | JB-DD-A3 | 33/34 | MC-DD-A3 | 17 | 110 | A3 | P-118 |  |  |  |  | equipment.json (MCC hardwired interface)
P-118 HS-STOP | P-118 | Motor interface (MCC) | Desalter mud-wash / recycle P-118 - Stop command (7.5 kW) | P-118 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 10 | FAR-100/MC-CDU-1-D01 | TB01-19/20 | JB-DD-A3 | 35/36 | MC-DD-A3 | 18 | 110 | A3 | P-118 |  |  |  |  | equipment.json (MCC hardwired interface)
X-101 HS-START | X-101 | Motor interface (MCC) | Demulsifier injection package X-101 - Start command (0.75 kW) | X-101 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 11 | FAR-100/MC-CDU-1-D01 | TB01-21/22 | JB-DD-B2 | 1/2 | MC-DD-B2 | 1 | 80 | B2 | X-101 |  |  |  |  | equipment.json (MCC hardwired interface)
X-101 HS-STOP | X-101 | Motor interface (MCC) | Demulsifier injection package X-101 - Stop command (0.75 kW) | X-101 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 12 | FAR-100/MC-CDU-1-D01 | TB01-23/24 | JB-DD-B2 | 3/4 | MC-DD-B2 | 2 | 80 | B2 | X-101 |  |  |  |  | equipment.json (MCC hardwired interface)
X-102 HS-START | X-102 | Motor interface (MCC) | Caustic injection package (desalted crude) X-102 - Start command (0.75 kW) | X-102 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO01 | 13 | FAR-100/MC-CDU-1-D01 | TB01-25/26 | JB-DD-B2 | 9/10 | MC-DD-B2 | 5 | 80 | B2 | X-102 |  |  |  |  | equipment.json (MCC hardwired interface)
X-102 HS-STOP | X-102 | Motor interface (MCC) | Caustic injection package (desalted crude) X-102 - Stop command (0.75 kW) | X-102 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 1 | FAR-100/MC-CDU-1-D01 | TB02-1/2 | JB-DD-B2 | 11/12 | MC-DD-B2 | 6 | 80 | B2 | X-102 |  |  |  |  | equipment.json (MCC hardwired interface)
P-102A HS-START | P-102A | Motor interface (MCC) | Desalted crude booster P-102A - Start command (710 kW) | P-102A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 2 | FAR-100/MC-CDU-1-D01 | TB02-3/4 | JB-DD-B3-1 | 17/18 | MC-DD-B3-1 | 9 | 100 | B3 | P-102A |  |  |  |  | equipment.json (MCC hardwired interface)
P-102A HS-STOP | P-102A | Motor interface (MCC) | Desalted crude booster P-102A - Stop command (710 kW) | P-102A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 3 | FAR-100/MC-CDU-1-D01 | TB02-5/6 | JB-DD-B3-1 | 19/20 | MC-DD-B3-1 | 10 | 100 | B3 | P-102A |  |  |  |  | equipment.json (MCC hardwired interface)
P-102B HS-START | P-102B | Motor interface (MCC) | Desalted crude booster P-102B - Start command (710 kW) | P-102B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 4 | FAR-100/MC-CDU-1-D01 | TB02-7/8 | JB-DD-B3-1 | 25/26 | MC-DD-B3-1 | 13 | 90 | B3 | P-102B |  |  |  |  | equipment.json (MCC hardwired interface)
P-102B HS-STOP | P-102B | Motor interface (MCC) | Desalted crude booster P-102B - Stop command (710 kW) | P-102B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 5 | FAR-100/MC-CDU-1-D01 | TB02-9/10 | JB-DD-B3-1 | 27/28 | MC-DD-B3-1 | 14 | 90 | B3 | P-102B |  |  |  |  | equipment.json (MCC hardwired interface)
X-103 HS-START | X-103 | Motor interface (MCC) | Neutraliser / filming amine package (atm OH) X-103 - Start command (0.75 kW) | X-103 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 6 | FAR-100/MC-CDU-1-D01 | TB02-11/12 | JB-DD-B4 | 1/2 | MC-DD-B4 | 1 | 160 | B4 | X-103 |  |  |  |  | equipment.json (MCC hardwired interface)
X-103 HS-STOP | X-103 | Motor interface (MCC) | Neutraliser / filming amine package (atm OH) X-103 - Stop command (0.75 kW) | X-103 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 7 | FAR-100/MC-CDU-1-D01 | TB02-13/14 | JB-DD-B4 | 3/4 | MC-DD-B4 | 2 | 160 | B4 | X-103 |  |  |  |  | equipment.json (MCC hardwired interface)
K-101A HS-START | K-101A | Motor interface (MCC) | H-101 forced-draft fan K-101A - Start command (90 kW) | K-101A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 8 | FAR-100/MC-CDU-1-D01 | TB02-15/16 | JB-DD-C1 | 1/2 | MC-DD-C1 | 1 | 90 | C1 | K-101A |  |  |  |  | equipment.json (MCC hardwired interface)
K-101A HS-STOP | K-101A | Motor interface (MCC) | H-101 forced-draft fan K-101A - Stop command (90 kW) | K-101A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 9 | FAR-100/MC-CDU-1-D01 | TB02-17/18 | JB-DD-C1 | 3/4 | MC-DD-C1 | 2 | 90 | C1 | K-101A |  |  |  |  | equipment.json (MCC hardwired interface)
K-101B HS-START | K-101B | Motor interface (MCC) | H-101 forced-draft fan K-101B - Start command (90 kW) | K-101B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 10 | FAR-100/MC-CDU-1-D01 | TB02-19/20 | JB-DD-C1 | 9/10 | MC-DD-C1 | 5 | 90 | C1 | K-101B |  |  |  |  | equipment.json (MCC hardwired interface)
K-101B HS-STOP | K-101B | Motor interface (MCC) | H-101 forced-draft fan K-101B - Stop command (90 kW) | K-101B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 11 | FAR-100/MC-CDU-1-D01 | TB02-21/22 | JB-DD-C1 | 11/12 | MC-DD-C1 | 6 | 90 | C1 | K-101B |  |  |  |  | equipment.json (MCC hardwired interface)
K-102A HS-START | K-102A | Motor interface (MCC) | H-101 induced-draft fan K-102A - Start command (200 kW) | K-102A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 12 | FAR-100/MC-CDU-1-D01 | TB02-23/24 | JB-DD-C1 | 17/18 | MC-DD-C1 | 9 | 100 | C1 | K-102A |  |  |  |  | equipment.json (MCC hardwired interface)
K-102A HS-STOP | K-102A | Motor interface (MCC) | H-101 induced-draft fan K-102A - Stop command (200 kW) | K-102A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO02 | 13 | FAR-100/MC-CDU-1-D01 | TB02-25/26 | JB-DD-C1 | 19/20 | MC-DD-C1 | 10 | 100 | C1 | K-102A |  |  |  |  | equipment.json (MCC hardwired interface)
K-102B HS-START | K-102B | Motor interface (MCC) | H-101 induced-draft fan K-102B - Start command (200 kW) | K-102B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO03 | 1 | FAR-100/MC-CDU-1-D01 | TB03-1/2 | JB-DD-C1 | 25/26 | MC-DD-C1 | 13 | 100 | C1 | K-102B |  |  |  |  | equipment.json (MCC hardwired interface)
K-102B HS-STOP | K-102B | Motor interface (MCC) | H-101 induced-draft fan K-102B - Stop command (200 kW) | K-102B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO03 | 2 | FAR-100/MC-CDU-1-D01 | TB03-3/4 | JB-DD-C1 | 27/28 | MC-DD-C1 | 14 | 100 | C1 | K-102B |  |  |  |  | equipment.json (MCC hardwired interface)
LY-9003 | LY-9003 | Level relay / output | P-119A/B start/stop (high / low level) via MCC | LIC-9003 | CFU-900-PR-PID-016 | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO03 | 3 | FAR-100/MC-CDU-1-D01 | TB03-5/6 | JB-DD-D5 | 1/2 | MC-DD-D5 | 1 | 250 | D5 | P-119A |  |  |  |  | instrument index
P-119A HS-START | P-119A | Motor interface (MCC) | Flare KO drum pump-out P-119A - Start command (7.5 kW) | P-119A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO03 | 4 | FAR-100/MC-CDU-1-D01 | TB03-7/8 | JB-DD-D5 | 3/4 | MC-DD-D5 | 2 | 250 | D5 | P-119A |  |  |  |  | equipment.json (MCC hardwired interface)
P-119A HS-STOP | P-119A | Motor interface (MCC) | Flare KO drum pump-out P-119A - Stop command (7.5 kW) | P-119A |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO03 | 5 | FAR-100/MC-CDU-1-D01 | TB03-9/10 | JB-DD-D5 | 5/6 | MC-DD-D5 | 3 | 250 | D5 | P-119A |  |  |  |  | equipment.json (MCC hardwired interface)
P-119B HS-START | P-119B | Motor interface (MCC) | Flare KO drum pump-out P-119B - Start command (7.5 kW) | P-119B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO03 | 6 | FAR-100/MC-CDU-1-D01 | TB03-11/12 | JB-DD-D5 | 11/12 | MC-DD-D5 | 6 | 250 | D5 | P-119B |  |  |  |  | equipment.json (MCC hardwired interface)
P-119B HS-STOP | P-119B | Motor interface (MCC) | Flare KO drum pump-out P-119B - Stop command (7.5 kW) | P-119B |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO03 | 7 | FAR-100/MC-CDU-1-D01 | TB03-13/14 | JB-DD-D5 | 13/14 | MC-DD-D5 | 7 | 250 | D5 | P-119B |  |  |  |  | equipment.json (MCC hardwired interface)
X-104 HS-START | X-104 | Motor interface (MCC) | Corrosion inhibitor package (VDU OH) X-104 - Start command (0.75 kW) | X-104 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO03 | 8 | FAR-100/MC-CDU-1-D01 | TB03-15/16 | JB-DD-F4 | 9/10 | MC-DD-F4 | 5 | 320 | F4 | X-104 |  |  |  |  | equipment.json (MCC hardwired interface)
X-104 HS-STOP | X-104 | Motor interface (MCC) | Corrosion inhibitor package (VDU OH) X-104 - Stop command (0.75 kW) | X-104 |  | DCS | CDU-1 | DO | 24 VDC interposing relay | CDU-1-DO03 | 9 | FAR-100/MC-CDU-1-D01 | TB03-17/18 | JB-DD-F4 | 11/12 | MC-DD-F4 | 6 | 320 | F4 | X-104 |  |  |  |  | equipment.json (MCC hardwired interface)
FT-1093 | FT-1093 | Flow transmitter | LPG product | FIC-1093 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 1 | FAR-100/MC-CDU-2-A01 | TB01-1/2 | JB-DA-B3 | 1/2 | MC-DA-B3 | 1 | 120 | B3 | P-115A |  |  | 0-20 | m3/h | instrument index
FT-1102 | FT-1102 | Flow transmitter | Light naphtha product | FIC-1102 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 2 | FAR-100/MC-CDU-2-A01 | TB01-3/4 | JB-DA-B3 | 3/4 | MC-DA-B3 | 2 | 110 | B3 | P-116A |  |  | 0-60 | m3/h | instrument index
FT-1107 | FT-1107 | Flow transmitter | Heavy naphtha product | FIC-1107 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 3 | FAR-100/MC-CDU-2-A01 | TB01-5/6 | JB-DA-B3 | 5/6 | MC-DA-B3 | 3 | 110 | B3 | P-117A |  |  | 0-150 | m3/h | instrument index
TI-1270 | TI-1270 | Temperature indicator | A-101 outlet temperature | TI-1270 | CFU-100-PR-PID-009 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 4 | FAR-100/MC-CDU-2-A01 | TB01-7/8 | JB-DA-B3 | 13/14 | MC-DA-B3 | 7 | 120 | B3 | A-101-B1 |  |  | 0-120 | C | instrument index
AT-1037 | AT-1037 | Analyser transmitter | OH sour water pH analyser | AIC-1037 | CFU-100-PR-PID-009 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 5 | FAR-100/MC-CDU-2-A01 | TB01-9/10 | JB-DA-B4-1 | 1/2 | MC-DA-B4-1 | 1 | 140 | B4 | D-102 |  |  | 0-14 | pH | instrument index
AT-1038 | AT-1038 | Analyser transmitter | Unstabilised naphtha D86 end point / RVP (online analyser) | AT-1038 | CFU-100-PR-PID-009 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 6 | FAR-100/MC-CDU-2-A01 | TB01-11/12 | JB-DA-B4-1 | 3/4 | MC-DA-B4-1 | 2 | 140 | B4 | D-102 |  |  | 100-250 | C (D86 EP) | instrument index
AT-1038 | AT-1038 | Analyser transmitter | Unstabilised naphtha D86 end point / RVP (online) | AT-1038 | (P&ID sheet 009) | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 7 | FAR-100/MC-CDU-2-A01 | TB01-13/14 | JB-DA-B4-1 | 5/6 | MC-DA-B4-1 | 3 | 140 | B4 | D-102 |  |  |  |  | I&C addition (add to index)
AT-1099 | AT-1099 | Analyser transmitter | LPG C5+ (process GC) | AT-1099 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 8 | FAR-100/MC-CDU-2-A01 | TB01-15/16 | JB-DA-B4-1 | 7/8 | MC-DA-B4-1 | 4 | 140 | B4 | C-105 |  |  | 0-5 | LV% C5+ | instrument index
AT-1099 | AT-1099 | Analyser transmitter | LPG C5+ (process GC) | AT-1099 | (P&ID sheet 010) | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 9 | FAR-100/MC-CDU-2-A01 | TB01-17/18 | JB-DA-B4-1 | 9/10 | MC-DA-B4-1 | 5 | 140 | B4 | C-105 |  |  |  |  | I&C addition (add to index)
AT-1108 | AT-1108 | Analyser transmitter | Light naphtha C6+ / RVP (process GC) | AT-1108 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 10 | FAR-100/MC-CDU-2-A01 | TB01-19/20 | JB-DA-B4-1 | 11/12 | MC-DA-B4-1 | 6 | 130 | B4 | C-106 |  |  | 0-10 | LV% C6+ | instrument index
AT-1108 | AT-1108 | Analyser transmitter | Light naphtha C6+ / RVP (process GC) | AT-1108 | (P&ID sheet 011) | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 11 | FAR-100/MC-CDU-2-A01 | TB01-21/22 | JB-DA-B4-1 | 13/14 | MC-DA-B4-1 | 7 | 130 | B4 | C-106 |  |  |  |  | I&C addition (add to index)
AT-1109 | AT-1109 | Analyser transmitter | Heavy naphtha IBP / C5- (process GC) | AT-1109 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 12 | FAR-100/MC-CDU-2-A01 | TB01-23/24 | JB-DA-B4-1 | 15/16 | MC-DA-B4-1 | 8 | 130 | B4 | C-106 |  |  | 0-5 | LV% C5- | instrument index
AT-1109 | AT-1109 | Analyser transmitter | Heavy naphtha IBP / C5- (process GC) | AT-1109 | (P&ID sheet 011) | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI01 | 13 | FAR-100/MC-CDU-2-A01 | TB01-25/26 | JB-DA-B4-1 | 17/18 | MC-DA-B4-1 | 9 | 130 | B4 | C-106 |  |  |  |  | I&C addition (add to index)
FT-1034 | FT-1034 | Flow transmitter | Unstabilised naphtha to C-105 | FIC-1034 | CFU-100-PR-PID-009 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 1 | FAR-100/MC-CDU-2-A01 | TB02-1/2 | JB-DA-B4-1 | 19/20 | MC-DA-B4-1 | 10 | 140 | B4 | C-105 |  |  | 0-250 | m3/h | instrument index
FT-1094 | FT-1094 | Flow transmitter | C-105 reflux | FIC-1094 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 2 | FAR-100/MC-CDU-2-A01 | TB02-3/4 | JB-DA-B4-1 | 21/22 | MC-DA-B4-1 | 11 | 140 | B4 | C-105 |  |  | 0-40 | m3/h | instrument index
FT-1096 | FT-1096 | Flow transmitter | HP steam to E-116 | FIC-1096 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 3 | FAR-100/MC-CDU-2-A01 | TB02-5/6 | JB-DA-B4-1 | 23/24 | MC-DA-B4-1 | 12 | 140 | B4 | E-116 |  |  | 0-30000 | kg/h | instrument index
FT-1103 | FT-1103 | Flow transmitter | C-106 reflux | FIC-1103 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 4 | FAR-100/MC-CDU-2-A01 | TB02-7/8 | JB-DA-B4-1 | 25/26 | MC-DA-B4-1 | 13 | 130 | B4 | C-106 |  |  | 0-120 | m3/h | instrument index
FT-1105 | FT-1105 | Flow transmitter | MP steam to E-117 | FIC-1105 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 5 | FAR-100/MC-CDU-2-A01 | TB02-9/10 | JB-DA-B4-1 | 27/28 | MC-DA-B4-1 | 14 | 140 | B4 | E-117 |  |  | 0-20000 | kg/h | instrument index
LT-1033 | LT-1033 | Level transmitter | D-102 hydrocarbon level | LIC-1033 | CFU-100-PR-PID-009 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 6 | FAR-100/MC-CDU-2-A01 | TB02-11/12 | JB-DA-B4-1 | 39/40 | MC-DA-B4-1 | 20 | 140 | B4 | D-102 |  |  | 0-100 | % | instrument index
LT-1035 | LT-1035 | Level transmitter | D-102 boot interface | LIC-1035 | CFU-100-PR-PID-009 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 7 | FAR-100/MC-CDU-2-A01 | TB02-13/14 | JB-DA-B4-1 | 41/42 | MC-DA-B4-1 | 21 | 140 | B4 | D-102 |  |  | 0-100 | % | instrument index
LT-1092 | LT-1092 | Level transmitter | D-105 level | LIC-1092 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 8 | FAR-100/MC-CDU-2-A01 | TB02-15/16 | JB-DA-B4-1 | 43/44 | MC-DA-B4-1 | 22 | 130 | B4 | D-105 |  |  | 0-100 | % | instrument index
LT-1097 | LT-1097 | Level transmitter | C-105 bottom level | LIC-1097 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 9 | FAR-100/MC-CDU-2-A01 | TB02-17/18 | JB-DA-B4-1 | 45/46 | MC-DA-B4-1 | 23 | 140 | B4 | C-105 |  |  | 0-100 | % | instrument index
LT-1098 | LT-1098 | Level transmitter | E-116 condensate pot level | LIC-1098 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 10 | FAR-100/MC-CDU-2-A01 | TB02-19/20 | JB-DA-B4-1 | 47/48 | MC-DA-B4-1 | 24 | 140 | B4 | E-116 |  |  | 0-100 | % | instrument index
LT-1101 | LT-1101 | Level transmitter | D-106 level | LIC-1101 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 11 | FAR-100/MC-CDU-2-A01 | TB02-21/22 | JB-DA-B4-2 | 1/2 | MC-DA-B4-2 | 1 | 120 | B4 | D-106 |  |  | 0-100 | % | instrument index
LT-1106 | LT-1106 | Level transmitter | C-106 bottom level | LIC-1106 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 12 | FAR-100/MC-CDU-2-A01 | TB02-23/24 | JB-DA-B4-2 | 3/4 | MC-DA-B4-2 | 2 | 130 | B4 | C-106 |  |  | 0-100 | % | instrument index
PDI-1287 | PDI-1287 | Differential pressure indicator | C-105 column dP | PDI-1287 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI02 | 13 | FAR-100/MC-CDU-2-A01 | TB02-25/26 | JB-DA-B4-2 | 19/20 | MC-DA-B4-2 | 10 | 140 | B4 | C-105 |  |  | 0-2.5 | bar | instrument index
PT-1032 | PT-1032 | Pressure transmitter | OH drum pressure (split range) | PIC-1032 | CFU-100-PR-PID-009 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 1 | FAR-100/MC-CDU-2-A01 | TB03-1/2 | JB-DA-B4-2 | 21/22 | MC-DA-B4-2 | 11 | 140 | B4 | D-102 |  |  | 0-3 | barg | instrument index
PT-1091 | PT-1091 | Pressure transmitter | C-105 pressure (hot-vapour bypass) | PIC-1091 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 2 | FAR-100/MC-CDU-2-A01 | TB03-3/4 | JB-DA-B4-2 | 23/24 | MC-DA-B4-2 | 12 | 140 | B4 | C-105 |  |  | 0-20 | barg | instrument index
PT-1100 | PT-1100 | Pressure transmitter | C-106 / D-106 pressure | PIC-1100 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 3 | FAR-100/MC-CDU-2-A01 | TB03-5/6 | JB-DA-B4-2 | 25/26 | MC-DA-B4-2 | 13 | 130 | B4 | C-106 |  |  | 0-4 | barg | instrument index
TI-1274 | TI-1274 | Temperature indicator | D-102 temperature | TI-1274 | CFU-100-PR-PID-009 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 4 | FAR-100/MC-CDU-2-A01 | TB03-7/8 | JB-DA-B4-2 | 39/40 | MC-DA-B4-2 | 20 | 140 | B4 | D-102 |  |  | 0-400 | C | instrument index
TI-1281 | TI-1281 | Temperature indicator | Stabiliser feed temperature | TI-1281 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 5 | FAR-100/MC-CDU-2-A01 | TB03-9/10 | JB-DA-B4-2 | 41/42 | MC-DA-B4-2 | 21 | 140 | B4 | C-105 |  |  | 0-150 | C | instrument index
TI-1294 | TI-1294 | Temperature indicator | C-106 bottoms temperature | TI-1294 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 6 | FAR-100/MC-CDU-2-A01 | TB03-11/12 | JB-DA-B4-2 | 43/44 | MC-DA-B4-2 | 22 | 130 | B4 | C-106 |  |  | 0-250 | C | instrument index
TT-1095 | TT-1095 | Temperature transmitter | C-105 sensitive tray temperature (RVP) | TIC-1095 | CFU-100-PR-PID-010 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 7 | FAR-100/MC-CDU-2-A01 | TB03-13/14 | JB-DA-B4-2 | 45/46 | MC-DA-B4-2 | 23 | 140 | B4 | C-105 |  |  | 0-300 | C | instrument index
TT-1104 | TT-1104 | Temperature transmitter | C-106 sensitive tray temperature | TIC-1104 | CFU-100-PR-PID-011 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 8 | FAR-100/MC-CDU-2-A01 | TB03-15/16 | JB-DA-B4-2 | 47/48 | MC-DA-B4-2 | 24 | 130 | B4 | C-106 |  |  | 0-250 | C | instrument index
FT-1044 | FT-1044 | Flow transmitter | BPA circulation | FIC-1044 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 9 | FAR-100/MC-CDU-2-A01 | TB03-17/18 | JB-DA-C3 | 1/2 | MC-DA-C3 | 1 | 160 | C3 | P-108A |  |  | 0-400 | m3/h | instrument index
FT-1052 | FT-1052 | Flow transmitter | Kerosene product | FIC-1052 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 10 | FAR-100/MC-CDU-2-A01 | TB03-19/20 | JB-DA-C3 | 3/4 | MC-DA-C3 | 2 | 170 | C3 | P-109A |  |  | 0-120 | m3/h | instrument index
FT-1062 | FT-1062 | Flow transmitter | Diesel product | FIC-1062 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 11 | FAR-100/MC-CDU-2-A01 | TB03-21/22 | JB-DA-C3 | 5/6 | MC-DA-C3 | 3 | 170 | C3 | P-110A |  |  | 0-150 | m3/h | instrument index
FT-1072 | FT-1072 | Flow transmitter | AGO product | FIC-1072 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 12 | FAR-100/MC-CDU-2-A01 | TB03-23/24 | JB-DA-C3 | 7/8 | MC-DA-C3 | 4 | 180 | C3 | P-111A |  |  | 0-80 | m3/h | instrument index
AT-1055 | AT-1055 | Analyser transmitter | Kerosene flash / freeze point (online analyser) | AT-1055 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI03 | 13 | FAR-100/MC-CDU-2-A01 | TB03-25/26 | JB-DA-C4-1 | 1/2 | MC-DA-C4-1 | 1 | 190 | C4 | C-103 |  |  | 0-100 | C (flash) | instrument index
AT-1055 | AT-1055 | Analyser transmitter | Kerosene flash / freeze point (online) | AT-1055 | (P&ID sheet 008) | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 1 | FAR-100/MC-CDU-2-A01 | TB04-1/2 | JB-DA-C4-1 | 3/4 | MC-DA-C4-1 | 2 | 190 | C4 | C-103 |  |  |  |  | I&C addition (add to index)
AT-1065 | AT-1065 | Analyser transmitter | Diesel D86 T95 / cloud point (online analyser) | AT-1065 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 2 | FAR-100/MC-CDU-2-A01 | TB04-3/4 | JB-DA-C4-1 | 5/6 | MC-DA-C4-1 | 3 | 190 | C4 | C-103 |  |  | 250-400 | C (D86 T95) | instrument index
AT-1065 | AT-1065 | Analyser transmitter | Diesel D86 T95 / cloud point (online) | AT-1065 | (P&ID sheet 008) | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 3 | FAR-100/MC-CDU-2-A01 | TB04-5/6 | JB-DA-C4-1 | 7/8 | MC-DA-C4-1 | 4 | 190 | C4 | C-103 |  |  |  |  | I&C addition (add to index)
AT-1075 | AT-1075 | Analyser transmitter | AGO D86 T95 / colour (online analyser) | AT-1075 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 4 | FAR-100/MC-CDU-2-A01 | TB04-7/8 | JB-DA-C4-1 | 9/10 | MC-DA-C4-1 | 5 | 190 | C4 | C-103 |  |  | 300-450 | C (D86 T95) | instrument index
AT-1075 | AT-1075 | Analyser transmitter | AGO D86 T95 / colour (online) | AT-1075 | (P&ID sheet 008) | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 5 | FAR-100/MC-CDU-2-A01 | TB04-9/10 | JB-DA-C4-1 | 11/12 | MC-DA-C4-1 | 6 | 190 | C4 | C-103 |  |  |  |  | I&C addition (add to index)
FI-1080 | FI-1080 | Flow indicator | Overflash (wash-zone liquid) flow | FI-1080 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 6 | FAR-100/MC-CDU-2-A01 | TB04-11/12 | JB-DA-C4-1 | 13/14 | MC-DA-C4-1 | 7 | 170 | C4 | C-101 |  |  | 0-100 | % | instrument index
FT-1031 | FT-1031 | Flow transmitter | C-101 reflux | FIC-1031 | CFU-100-PR-PID-009 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 7 | FAR-100/MC-CDU-2-A01 | TB04-13/14 | JB-DA-C4-1 | 15/16 | MC-DA-C4-1 | 8 | 170 | C4 | C-101 |  |  | 0-200 | m3/h | instrument index
FT-1050 | FT-1050 | Flow transmitter | Kerosene draw to C-102 | FIC-1050 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 8 | FAR-100/MC-CDU-2-A01 | TB04-15/16 | JB-DA-C4-1 | 17/18 | MC-DA-C4-1 | 9 | 190 | C4 | C-102 |  |  | 0-200 | m3/h | instrument index
FT-1054 | FT-1054 | Flow transmitter | C-102 stripping steam | FIC-1054 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 9 | FAR-100/MC-CDU-2-A01 | TB04-17/18 | JB-DA-C4-1 | 19/20 | MC-DA-C4-1 | 10 | 190 | C4 | C-102 |  |  | 0-2000 | kg/h | instrument index
FT-1060 | FT-1060 | Flow transmitter | Diesel draw to C-103 | FIC-1060 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 10 | FAR-100/MC-CDU-2-A01 | TB04-19/20 | JB-DA-C4-1 | 21/22 | MC-DA-C4-1 | 11 | 190 | C4 | C-103 |  |  | 0-250 | m3/h | instrument index
FT-1064 | FT-1064 | Flow transmitter | C-103 stripping steam | FIC-1064 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 11 | FAR-100/MC-CDU-2-A01 | TB04-21/22 | JB-DA-C4-1 | 23/24 | MC-DA-C4-1 | 12 | 190 | C4 | C-103 |  |  | 0-2500 | kg/h | instrument index
FT-1070 | FT-1070 | Flow transmitter | AGO draw to C-104 | FIC-1070 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 12 | FAR-100/MC-CDU-2-A01 | TB04-23/24 | JB-DA-C4-1 | 25/26 | MC-DA-C4-1 | 13 | 200 | C4 | C-104 |  |  | 0-120 | m3/h | instrument index
FT-1074 | FT-1074 | Flow transmitter | C-104 stripping steam | FIC-1074 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI04 | 13 | FAR-100/MC-CDU-2-A01 | TB04-25/26 | JB-DA-C4-1 | 27/28 | MC-DA-C4-1 | 14 | 200 | C4 | C-104 |  |  | 0-1200 | kg/h | instrument index
FT-1080 | FT-1080 | Flow transmitter | Overflash (wash-zone liquid) flow | FI-1080 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 1 | FAR-100/MC-CDU-2-A01 | TB05-1/2 | JB-DA-C4-1 | 29/30 | MC-DA-C4-1 | 15 | 170 | C4 | C-101 |  |  | 0-40 | m3/h | instrument index
FT-1081 | FT-1081 | Flow transmitter | C-101 bottom stripping steam | FIC-1081 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 2 | FAR-100/MC-CDU-2-A01 | TB05-3/4 | JB-DA-C4-1 | 31/32 | MC-DA-C4-1 | 16 | 170 | C4 | C-101 |  |  | 0-10000 | kg/h | instrument index
LT-1051 | LT-1051 | Level transmitter | C-102 bottom level | LIC-1051 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 3 | FAR-100/MC-CDU-2-A01 | TB05-5/6 | JB-DA-C4-2 | 1/2 | MC-DA-C4-2 | 1 | 190 | C4 | C-102 |  |  | 0-100 | % | instrument index
LT-1061 | LT-1061 | Level transmitter | C-103 bottom level | LIC-1061 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 4 | FAR-100/MC-CDU-2-A01 | TB05-7/8 | JB-DA-C4-2 | 3/4 | MC-DA-C4-2 | 2 | 190 | C4 | C-103 |  |  | 0-100 | % | instrument index
LT-1071 | LT-1071 | Level transmitter | C-104 bottom level | LIC-1071 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 5 | FAR-100/MC-CDU-2-A01 | TB05-9/10 | JB-DA-C4-2 | 5/6 | MC-DA-C4-2 | 3 | 200 | C4 | C-104 |  |  | 0-100 | % | instrument index
LT-1082 | LT-1082 | Level transmitter | C-101 bottom level | LIC-1082 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 6 | FAR-100/MC-CDU-2-A01 | TB05-11/12 | JB-DA-C4-2 | 7/8 | MC-DA-C4-2 | 4 | 170 | C4 | C-101 |  |  | 0-100 | % | instrument index
PDI-1237 | PDI-1237 | Differential pressure indicator | C-101 column dP (top - flash zone) | PDI-1237 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 7 | FAR-100/MC-CDU-2-A01 | TB05-13/14 | JB-DA-C4-2 | 9/10 | MC-DA-C4-2 | 5 | 170 | C4 | C-101 |  |  | 0-2.5 | bar | instrument index
PT-1236 | PT-1236 | Pressure transmitter | C-101 flash zone pressure | PT-1236 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 8 | FAR-100/MC-CDU-2-A01 | TB05-15/16 | JB-DA-C4-2 | 11/12 | MC-DA-C4-2 | 6 | 170 | C4 | C-101 |  |  | 0-5 | barg | instrument index
PT-1243 | PT-1243 | Pressure transmitter | C-101 top pressure | PT-1243 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 9 | FAR-100/MC-CDU-2-A01 | TB05-17/18 | JB-DA-C4-2 | 13/14 | MC-DA-C4-2 | 7 | 170 | C4 | C-101 |  |  | 0-5 | barg | instrument index
TI-1234 | TI-1234 | Temperature indicator | C-101 flash zone feed temperature (COT) | TI-1234 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 10 | FAR-100/MC-CDU-2-A01 | TB05-19/20 | JB-DA-C4-2 | 15/16 | MC-DA-C4-2 | 8 | 170 | C4 | C-101 |  |  | 0-500 | C | instrument index
TI-1235 | TI-1235 | Temperature indicator | AGO draw temperature | TI-1235 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 11 | FAR-100/MC-CDU-2-A01 | TB05-21/22 | JB-DA-C4-2 | 17/18 | MC-DA-C4-2 | 9 | 170 | C4 | C-101 |  |  | 0-500 | C | instrument index
TI-1242 | TI-1242 | Temperature indicator | C-101 bottoms temperature | TI-1242 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 12 | FAR-100/MC-CDU-2-A01 | TB05-23/24 | JB-DA-C4-2 | 19/20 | MC-DA-C4-2 | 10 | 170 | C4 | C-101 |  |  | 0-500 | C | instrument index
TI-1244 | TI-1244 | Temperature indicator | Kero draw temperature | TI-1244 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI05 | 13 | FAR-100/MC-CDU-2-A01 | TB05-25/26 | JB-DA-C4-2 | 21/22 | MC-DA-C4-2 | 11 | 170 | C4 | C-101 |  |  | 0-300 | C | instrument index
TI-1245 | TI-1245 | Temperature indicator | Dsl draw temperature | TI-1245 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 1 | FAR-100/MC-CDU-2-A01 | TB06-1/2 | JB-DA-C4-2 | 23/24 | MC-DA-C4-2 | 12 | 170 | C4 | C-101 |  |  | 0-400 | C | instrument index
TI-1248 | TI-1248 | Temperature indicator | TPA draw temperature | TI-1248 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 2 | FAR-100/MC-CDU-2-A01 | TB06-3/4 | JB-DA-C4-2 | 25/26 | MC-DA-C4-2 | 13 | 170 | C4 | C-101 |  |  | 0-250 | C | instrument index
TI-1251 | TI-1251 | Temperature indicator | MPA draw temperature | TI-1251 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 3 | FAR-100/MC-CDU-2-A01 | TB06-5/6 | JB-DA-C4-2 | 27/28 | MC-DA-C4-2 | 14 | 170 | C4 | C-101 |  |  | 0-400 | C | instrument index
TI-1254 | TI-1254 | Temperature indicator | BPA draw temperature | TI-1254 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 4 | FAR-100/MC-CDU-2-A01 | TB06-7/8 | JB-DA-C4-2 | 29/30 | MC-DA-C4-2 | 15 | 170 | C4 | C-101 |  |  | 0-500 | C | instrument index
TI-1259 | TI-1259 | Temperature indicator | C-102 product rundown temperature | TI-1259 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 5 | FAR-100/MC-CDU-2-A01 | TB06-9/10 | JB-DA-C4-2 | 31/32 | MC-DA-C4-2 | 16 | 190 | C4 | C-102 |  |  | 0-100 | C | instrument index
TI-1264 | TI-1264 | Temperature indicator | C-103 product rundown temperature | TI-1264 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 6 | FAR-100/MC-CDU-2-A01 | TB06-11/12 | JB-DA-C4-2 | 33/34 | MC-DA-C4-2 | 17 | 190 | C4 | C-103 |  |  | 0-120 | C | instrument index
TI-1269 | TI-1269 | Temperature indicator | C-104 product rundown temperature | TI-1269 | CFU-100-PR-PID-008 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 7 | FAR-100/MC-CDU-2-A01 | TB06-13/14 | JB-DA-C4-2 | 35/36 | MC-DA-C4-2 | 18 | 200 | C4 | C-104 |  |  | 0-120 | C | instrument index
TT-1030 | TT-1030 | Temperature transmitter | C-101 top temperature (naphtha end point) | TIC-1030 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 8 | FAR-100/MC-CDU-2-A01 | TB06-15/16 | JB-DA-C4-2 | 37/38 | MC-DA-C4-2 | 19 | 170 | C4 | C-101 |  |  | 0-200 | C | instrument index
TT-9005 | TT-9005 | Temperature transmitter | Ambient air temperature (APC DV) | TT-9005 | (P&ID sheet 016) | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 9 | FAR-100/MC-CDU-2-A01 | TB06-17/18 | JB-DA-D1 | 17/18 | MC-DA-D1 | 9 | 140 | D1 | D-103 |  |  |  |  | I&C addition (add to index)
FT-1040 | FT-1040 | Flow transmitter | TPA circulation | FIC-1040 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 10 | FAR-100/MC-CDU-2-A01 | TB06-19/20 | JB-DA-D3 | 1/2 | MC-DA-D3 | 1 | 190 | D3 | P-106A |  |  | 0-400 | m3/h | instrument index
FT-1042 | FT-1042 | Flow transmitter | MPA circulation | FIC-1042 | CFU-100-PR-PID-007 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 11 | FAR-100/MC-CDU-2-A01 | TB06-21/22 | JB-DA-D3 | 3/4 | MC-DA-D3 | 2 | 200 | D3 | P-107A |  |  | 0-500 | m3/h | instrument index
FT-1083 | FT-1083 | Flow transmitter | Atm. residue to H-201 | FIC-1083 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 12 | FAR-100/MC-CDU-2-A01 | TB06-23/24 | JB-DA-E2-1 | 5/6 | MC-DA-E2-1 | 3 | 190 | E2 | H-201 |  |  | 0-500 | m3/h | instrument index
TI-1240 | TI-1240 | Temperature indicator | AR to H-201 temperature | TI-1240 | CFU-100-PR-PID-006 | DCS | CDU-2 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | CDU-2-AI06 | 13 | FAR-100/MC-CDU-2-A01 | TB06-25/26 | JB-DA-E2-1 | 41/42 | MC-DA-E2-1 | 21 | 190 | E2 | H-201 |  |  | 0-500 | C | instrument index
FV-1093 | FV-1093 | Flow control valve | LPG product - Valve positioner / output | FIC-1093 | CFU-100-PR-PID-010 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO01 | 1 | FAR-100/MC-CDU-2-A01 | TB01-1/2 | JB-DA-B3 | 7/8 | MC-DA-B3 | 4 | 120 | B3 | P-115A |  |  |  |  | instrument index
FV-1102 | FV-1102 | Flow control valve | Light naphtha product - Valve positioner / output | FIC-1102 | CFU-100-PR-PID-011 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO01 | 2 | FAR-100/MC-CDU-2-A01 | TB01-3/4 | JB-DA-B3 | 9/10 | MC-DA-B3 | 5 | 110 | B3 | P-116A |  |  |  |  | instrument index
FV-1107 | FV-1107 | Flow control valve | Heavy naphtha product - Valve positioner / output | FIC-1107 | CFU-100-PR-PID-011 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO01 | 3 | FAR-100/MC-CDU-2-A01 | TB01-5/6 | JB-DA-B3 | 11/12 | MC-DA-B3 | 6 | 110 | B3 | P-117A |  |  |  |  | instrument index
FV-1034 | FV-1034 | Flow control valve | Unstabilised naphtha to C-105 - Valve positioner / output | FIC-1034 | CFU-100-PR-PID-009 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO01 | 4 | FAR-100/MC-CDU-2-A01 | TB01-7/8 | JB-DA-B4-1 | 29/30 | MC-DA-B4-1 | 15 | 140 | B4 | C-105 |  |  |  |  | instrument index
FV-1094 | FV-1094 | Flow control valve | C-105 reflux - Valve positioner / output | FIC-1094 | CFU-100-PR-PID-010 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO01 | 5 | FAR-100/MC-CDU-2-A01 | TB01-9/10 | JB-DA-B4-1 | 31/32 | MC-DA-B4-1 | 16 | 140 | B4 | C-105 |  |  |  |  | instrument index
FV-1096 | FV-1096 | Flow control valve | HP steam to E-116 - Valve positioner / output | FIC-1096 | CFU-100-PR-PID-010 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO01 | 6 | FAR-100/MC-CDU-2-A01 | TB01-11/12 | JB-DA-B4-1 | 33/34 | MC-DA-B4-1 | 17 | 140 | B4 | E-116 |  |  |  |  | instrument index
FV-1103 | FV-1103 | Flow control valve | C-106 reflux - Valve positioner / output | FIC-1103 | CFU-100-PR-PID-011 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO02 | 1 | FAR-100/MC-CDU-2-A01 | TB02-1/2 | JB-DA-B4-1 | 35/36 | MC-DA-B4-1 | 18 | 130 | B4 | C-106 |  |  |  |  | instrument index
FV-1105 | FV-1105 | Flow control valve | MP steam to E-117 - Valve positioner / output | FIC-1105 | CFU-100-PR-PID-011 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO02 | 2 | FAR-100/MC-CDU-2-A01 | TB02-3/4 | JB-DA-B4-1 | 37/38 | MC-DA-B4-1 | 19 | 140 | B4 | E-117 |  |  |  |  | instrument index
LV-1035 | LV-1035 | Level control valve | D-102 boot interface - Valve positioner / output | LIC-1035 | CFU-100-PR-PID-009 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO02 | 3 | FAR-100/MC-CDU-2-A01 | TB02-5/6 | JB-DA-B4-2 | 9/10 | MC-DA-B4-2 | 5 | 140 | B4 | D-102 |  |  |  |  | instrument index
LV-1097 | LV-1097 | Level control valve | C-105 bottom level - Valve positioner / output | LIC-1097 | CFU-100-PR-PID-010 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO02 | 4 | FAR-100/MC-CDU-2-A01 | TB02-7/8 | JB-DA-B4-2 | 11/12 | MC-DA-B4-2 | 6 | 140 | B4 | C-105 |  |  |  |  | instrument index
LV-1098 | LV-1098 | Level control valve | E-116 condensate pot level - Valve positioner / output | LIC-1098 | CFU-100-PR-PID-010 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO02 | 5 | FAR-100/MC-CDU-2-A01 | TB02-9/10 | JB-DA-B4-2 | 13/14 | MC-DA-B4-2 | 7 | 140 | B4 | E-116 |  |  |  |  | instrument index
PV-1032A | PV-1032A | Pressure control valve | OH drum pressure (split range) - Valve positioner / output | PIC-1032 | CFU-100-PR-PID-009 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO02 | 6 | FAR-100/MC-CDU-2-A01 | TB02-11/12 | JB-DA-B4-2 | 29/30 | MC-DA-B4-2 | 15 | 140 | B4 | D-102 |  |  |  |  | instrument index
PV-1091 | PV-1091 | Pressure control valve | C-105 pressure (hot-vapour bypass) - Valve positioner / output | PIC-1091 | CFU-100-PR-PID-010 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO03 | 1 | FAR-100/MC-CDU-2-A01 | TB03-1/2 | JB-DA-B4-2 | 31/32 | MC-DA-B4-2 | 16 | 140 | B4 | C-105 |  |  |  |  | instrument index
PV-1100 | PV-1100 | Pressure control valve | C-106 / D-106 pressure - Valve positioner / output | PIC-1100 | CFU-100-PR-PID-011 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO03 | 2 | FAR-100/MC-CDU-2-A01 | TB03-3/4 | JB-DA-B4-2 | 33/34 | MC-DA-B4-2 | 17 | 130 | B4 | C-106 |  |  |  |  | instrument index
FV-1044 | FV-1044 | Flow control valve | BPA circulation - Valve positioner / output | FIC-1044 | CFU-100-PR-PID-007 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO03 | 3 | FAR-100/MC-CDU-2-A01 | TB03-5/6 | JB-DA-C3 | 9/10 | MC-DA-C3 | 5 | 160 | C3 | P-108A |  |  |  |  | instrument index
FV-1052 | FV-1052 | Flow control valve | Kerosene product - Valve positioner / output | FIC-1052 | CFU-100-PR-PID-008 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO03 | 4 | FAR-100/MC-CDU-2-A01 | TB03-7/8 | JB-DA-C3 | 11/12 | MC-DA-C3 | 6 | 170 | C3 | P-109A |  |  |  |  | instrument index
FV-1062 | FV-1062 | Flow control valve | Diesel product - Valve positioner / output | FIC-1062 | CFU-100-PR-PID-008 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO03 | 5 | FAR-100/MC-CDU-2-A01 | TB03-9/10 | JB-DA-C3 | 13/14 | MC-DA-C3 | 7 | 170 | C3 | P-110A |  |  |  |  | instrument index
FV-1072 | FV-1072 | Flow control valve | AGO product - Valve positioner / output | FIC-1072 | CFU-100-PR-PID-008 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO03 | 6 | FAR-100/MC-CDU-2-A01 | TB03-11/12 | JB-DA-C3 | 15/16 | MC-DA-C3 | 8 | 180 | C3 | P-111A |  |  |  |  | instrument index
FV-1031 | FV-1031 | Flow control valve | C-101 reflux - Valve positioner / output | FIC-1031 | CFU-100-PR-PID-009 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO04 | 1 | FAR-100/MC-CDU-2-A01 | TB04-1/2 | JB-DA-C4-1 | 33/34 | MC-DA-C4-1 | 17 | 170 | C4 | C-101 |  |  |  |  | instrument index
FV-1050 | FV-1050 | Flow control valve | Kerosene draw to C-102 - Valve positioner / output | FIC-1050 | CFU-100-PR-PID-008 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO04 | 2 | FAR-100/MC-CDU-2-A01 | TB04-3/4 | JB-DA-C4-1 | 35/36 | MC-DA-C4-1 | 18 | 190 | C4 | C-102 |  |  |  |  | instrument index
FV-1054 | FV-1054 | Flow control valve | C-102 stripping steam - Valve positioner / output | FIC-1054 | CFU-100-PR-PID-008 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO04 | 3 | FAR-100/MC-CDU-2-A01 | TB04-5/6 | JB-DA-C4-1 | 37/38 | MC-DA-C4-1 | 19 | 190 | C4 | C-102 |  |  |  |  | instrument index
FV-1060 | FV-1060 | Flow control valve | Diesel draw to C-103 - Valve positioner / output | FIC-1060 | CFU-100-PR-PID-008 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO04 | 4 | FAR-100/MC-CDU-2-A01 | TB04-7/8 | JB-DA-C4-1 | 39/40 | MC-DA-C4-1 | 20 | 190 | C4 | C-103 |  |  |  |  | instrument index
FV-1064 | FV-1064 | Flow control valve | C-103 stripping steam - Valve positioner / output | FIC-1064 | CFU-100-PR-PID-008 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO04 | 5 | FAR-100/MC-CDU-2-A01 | TB04-9/10 | JB-DA-C4-1 | 41/42 | MC-DA-C4-1 | 21 | 190 | C4 | C-103 |  |  |  |  | instrument index
FV-1070 | FV-1070 | Flow control valve | AGO draw to C-104 - Valve positioner / output | FIC-1070 | CFU-100-PR-PID-008 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO04 | 6 | FAR-100/MC-CDU-2-A01 | TB04-11/12 | JB-DA-C4-1 | 43/44 | MC-DA-C4-1 | 22 | 200 | C4 | C-104 |  |  |  |  | instrument index
FV-1074 | FV-1074 | Flow control valve | C-104 stripping steam - Valve positioner / output | FIC-1074 | CFU-100-PR-PID-008 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO05 | 1 | FAR-100/MC-CDU-2-A01 | TB05-1/2 | JB-DA-C4-1 | 45/46 | MC-DA-C4-1 | 23 | 200 | C4 | C-104 |  |  |  |  | instrument index
FV-1081 | FV-1081 | Flow control valve | C-101 bottom stripping steam - Valve positioner / output | FIC-1081 | CFU-100-PR-PID-006 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO05 | 2 | FAR-100/MC-CDU-2-A01 | TB05-3/4 | JB-DA-C4-1 | 47/48 | MC-DA-C4-1 | 24 | 170 | C4 | C-101 |  |  |  |  | instrument index
FV-1040 | FV-1040 | Flow control valve | TPA circulation - Valve positioner / output | FIC-1040 | CFU-100-PR-PID-007 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO05 | 3 | FAR-100/MC-CDU-2-A01 | TB05-5/6 | JB-DA-D3 | 5/6 | MC-DA-D3 | 3 | 190 | D3 | P-106A |  |  |  |  | instrument index
FV-1042 | FV-1042 | Flow control valve | MPA circulation - Valve positioner / output | FIC-1042 | CFU-100-PR-PID-007 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO05 | 4 | FAR-100/MC-CDU-2-A01 | TB05-7/8 | JB-DA-D3 | 7/8 | MC-DA-D3 | 4 | 200 | D3 | P-107A |  |  |  |  | instrument index
FV-1083 | FV-1083 | Flow control valve | Atm. residue to H-201 - Valve positioner / output | FIC-1083 | CFU-100-PR-PID-006 | DCS | CDU-2 | AO | 4-20 mA HART to smart positioner | CDU-2-AO05 | 5 | FAR-100/MC-CDU-2-A01 | TB05-9/10 | JB-DA-E2-1 | 21/22 | MC-DA-E2-1 | 11 | 190 | E2 | H-201 |  |  |  |  | instrument index
A-106 XA | A-106 | Motor interface (MCC) | Stabiliser overhead condenser A-106 - Motor fault / not available (11 kW) | A-106 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 1 | FAR-100/MC-CDU-2-D01 | TB01-1/2 | JB-DD-B3-1 | 5/6 | MC-DD-B3-1 | 3 | 100 | B3 | A-106 |  |  |  |  | equipment.json (MCC hardwired interface)
A-106 XL | A-106 | Motor interface (MCC) | Stabiliser overhead condenser A-106 - Motor running (11 kW) | A-106 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 2 | FAR-100/MC-CDU-2-D01 | TB01-3/4 | JB-DD-B3-1 | 7/8 | MC-DD-B3-1 | 4 | 100 | B3 | A-106 |  |  |  |  | equipment.json (MCC hardwired interface)
A-108 XA | A-108 | Motor interface (MCC) | Heavy naphtha product cooler A-108 - Motor fault / not available (30 kW) | A-108 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 3 | FAR-100/MC-CDU-2-D01 | TB01-5/6 | JB-DD-B3-1 | 13/14 | MC-DD-B3-1 | 7 | 110 | B3 | A-108 |  |  |  |  | equipment.json (MCC hardwired interface)
A-108 XL | A-108 | Motor interface (MCC) | Heavy naphtha product cooler A-108 - Motor running (30 kW) | A-108 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 4 | FAR-100/MC-CDU-2-D01 | TB01-7/8 | JB-DD-B3-1 | 15/16 | MC-DD-B3-1 | 8 | 110 | B3 | A-108 |  |  |  |  | equipment.json (MCC hardwired interface)
P-103A XA | P-103A | Motor interface (MCC) | Atm. reflux P-103A - Motor fault / not available (55 kW) | P-103A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 5 | FAR-100/MC-CDU-2-D01 | TB01-9/10 | JB-DD-B3-1 | 37/38 | MC-DD-B3-1 | 19 | 130 | B3 | P-103A |  |  |  |  | equipment.json (MCC hardwired interface)
P-103A XL | P-103A | Motor interface (MCC) | Atm. reflux P-103A - Motor running (55 kW) | P-103A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 6 | FAR-100/MC-CDU-2-D01 | TB01-11/12 | JB-DD-B3-1 | 39/40 | MC-DD-B3-1 | 20 | 130 | B3 | P-103A |  |  |  |  | equipment.json (MCC hardwired interface)
P-103B XA | P-103B | Motor interface (MCC) | Atm. reflux P-103B - Motor fault / not available (55 kW) | P-103B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 7 | FAR-100/MC-CDU-2-D01 | TB01-13/14 | JB-DD-B3-1 | 45/46 | MC-DD-B3-1 | 23 | 130 | B3 | P-103B |  |  |  |  | equipment.json (MCC hardwired interface)
P-103B XL | P-103B | Motor interface (MCC) | Atm. reflux P-103B - Motor running (55 kW) | P-103B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 8 | FAR-100/MC-CDU-2-D01 | TB01-15/16 | JB-DD-B3-1 | 47/48 | MC-DD-B3-1 | 24 | 130 | B3 | P-103B |  |  |  |  | equipment.json (MCC hardwired interface)
P-104A XA | P-104A | Motor interface (MCC) | Unstabilised naphtha P-104A - Motor fault / not available (160 kW) | P-104A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 9 | FAR-100/MC-CDU-2-D01 | TB01-17/18 | JB-DD-B3-2 | 5/6 | MC-DD-B3-2 | 3 | 140 | B3 | P-104A |  |  |  |  | equipment.json (MCC hardwired interface)
P-104A XL | P-104A | Motor interface (MCC) | Unstabilised naphtha P-104A - Motor running (160 kW) | P-104A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 10 | FAR-100/MC-CDU-2-D01 | TB01-19/20 | JB-DD-B3-2 | 7/8 | MC-DD-B3-2 | 4 | 140 | B3 | P-104A |  |  |  |  | equipment.json (MCC hardwired interface)
P-115A XA | P-115A | Motor interface (MCC) | Stabiliser reflux / LPG P-115A - Motor fault / not available (18.5 kW) | P-115A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 11 | FAR-100/MC-CDU-2-D01 | TB01-21/22 | JB-DD-B3-2 | 13/14 | MC-DD-B3-2 | 7 | 120 | B3 | P-115A |  |  |  |  | equipment.json (MCC hardwired interface)
P-115A XL | P-115A | Motor interface (MCC) | Stabiliser reflux / LPG P-115A - Motor running (18.5 kW) | P-115A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 12 | FAR-100/MC-CDU-2-D01 | TB01-23/24 | JB-DD-B3-2 | 15/16 | MC-DD-B3-2 | 8 | 120 | B3 | P-115A |  |  |  |  | equipment.json (MCC hardwired interface)
P-115B XA | P-115B | Motor interface (MCC) | Stabiliser reflux / LPG P-115B - Motor fault / not available (18.5 kW) | P-115B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 13 | FAR-100/MC-CDU-2-D01 | TB01-25/26 | JB-DD-B3-2 | 21/22 | MC-DD-B3-2 | 11 | 120 | B3 | P-115B |  |  |  |  | equipment.json (MCC hardwired interface)
P-115B XL | P-115B | Motor interface (MCC) | Stabiliser reflux / LPG P-115B - Motor running (18.5 kW) | P-115B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 14 | FAR-100/MC-CDU-2-D01 | TB01-27/28 | JB-DD-B3-2 | 23/24 | MC-DD-B3-2 | 12 | 120 | B3 | P-115B |  |  |  |  | equipment.json (MCC hardwired interface)
P-116A XA | P-116A | Motor interface (MCC) | Splitter reflux / LN P-116A - Motor fault / not available (55 kW) | P-116A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 15 | FAR-100/MC-CDU-2-D01 | TB01-29/30 | JB-DD-B3-2 | 29/30 | MC-DD-B3-2 | 15 | 110 | B3 | P-116A |  |  |  |  | equipment.json (MCC hardwired interface)
P-116A XL | P-116A | Motor interface (MCC) | Splitter reflux / LN P-116A - Motor running (55 kW) | P-116A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 16 | FAR-100/MC-CDU-2-D01 | TB01-31/32 | JB-DD-B3-2 | 31/32 | MC-DD-B3-2 | 16 | 110 | B3 | P-116A |  |  |  |  | equipment.json (MCC hardwired interface)
P-116B XA | P-116B | Motor interface (MCC) | Splitter reflux / LN P-116B - Motor fault / not available (55 kW) | P-116B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 17 | FAR-100/MC-CDU-2-D01 | TB01-33/34 | JB-DD-B3-2 | 37/38 | MC-DD-B3-2 | 19 | 110 | B3 | P-116B |  |  |  |  | equipment.json (MCC hardwired interface)
P-116B XL | P-116B | Motor interface (MCC) | Splitter reflux / LN P-116B - Motor running (55 kW) | P-116B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 18 | FAR-100/MC-CDU-2-D01 | TB01-35/36 | JB-DD-B3-2 | 39/40 | MC-DD-B3-2 | 20 | 110 | B3 | P-116B |  |  |  |  | equipment.json (MCC hardwired interface)
P-117A XA | P-117A | Motor interface (MCC) | Heavy naphtha product P-117A - Motor fault / not available (45 kW) | P-117A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 19 | FAR-100/MC-CDU-2-D01 | TB01-37/38 | JB-DD-B3-2 | 45/46 | MC-DD-B3-2 | 23 | 110 | B3 | P-117A |  |  |  |  | equipment.json (MCC hardwired interface)
P-117A XL | P-117A | Motor interface (MCC) | Heavy naphtha product P-117A - Motor running (45 kW) | P-117A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 20 | FAR-100/MC-CDU-2-D01 | TB01-39/40 | JB-DD-B3-2 | 47/48 | MC-DD-B3-2 | 24 | 110 | B3 | P-117A |  |  |  |  | equipment.json (MCC hardwired interface)
P-117B XA | P-117B | Motor interface (MCC) | Heavy naphtha product P-117B - Motor fault / not available (45 kW) | P-117B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 21 | FAR-100/MC-CDU-2-D01 | TB01-41/42 | JB-DD-B3-3 | 5/6 | MC-DD-B3-3 | 3 | 110 | B3 | P-117B |  |  |  |  | equipment.json (MCC hardwired interface)
P-117B XL | P-117B | Motor interface (MCC) | Heavy naphtha product P-117B - Motor running (45 kW) | P-117B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 22 | FAR-100/MC-CDU-2-D01 | TB01-43/44 | JB-DD-B3-3 | 7/8 | MC-DD-B3-3 | 4 | 110 | B3 | P-117B |  |  |  |  | equipment.json (MCC hardwired interface)
A-103 XA | A-103 | Motor interface (MCC) | Kero cooler A-103 - Motor fault / not available (11 kW) | A-103 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 23 | FAR-100/MC-CDU-2-D01 | TB01-45/46 | JB-DD-C3-1 | 5/6 | MC-DD-C3-1 | 3 | 160 | C3 | A-103 |  |  |  |  | equipment.json (MCC hardwired interface)
A-103 XL | A-103 | Motor interface (MCC) | Kero cooler A-103 - Motor running (11 kW) | A-103 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 24 | FAR-100/MC-CDU-2-D01 | TB01-47/48 | JB-DD-C3-1 | 7/8 | MC-DD-C3-1 | 4 | 160 | C3 | A-103 |  |  |  |  | equipment.json (MCC hardwired interface)
A-104 XA | A-104 | Motor interface (MCC) | Diesel cooler A-104 - Motor fault / not available (18.5 kW) | A-104 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 25 | FAR-100/MC-CDU-2-D01 | TB01-49/50 | JB-DD-C3-1 | 13/14 | MC-DD-C3-1 | 7 | 170 | C3 | A-104 |  |  |  |  | equipment.json (MCC hardwired interface)
A-104 XL | A-104 | Motor interface (MCC) | Diesel cooler A-104 - Motor running (18.5 kW) | A-104 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI01 | 26 | FAR-100/MC-CDU-2-D01 | TB01-51/52 | JB-DD-C3-1 | 15/16 | MC-DD-C3-1 | 8 | 170 | C3 | A-104 |  |  |  |  | equipment.json (MCC hardwired interface)
P-104B XA | P-104B | Motor interface (MCC) | Unstabilised naphtha P-104B - Motor fault / not available (160 kW) | P-104B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 1 | FAR-100/MC-CDU-2-D01 | TB02-1/2 | JB-DD-C3-1 | 21/22 | MC-DD-C3-1 | 11 | 140 | C3 | P-104B |  |  |  |  | equipment.json (MCC hardwired interface)
P-104B XL | P-104B | Motor interface (MCC) | Unstabilised naphtha P-104B - Motor running (160 kW) | P-104B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 2 | FAR-100/MC-CDU-2-D01 | TB02-3/4 | JB-DD-C3-1 | 23/24 | MC-DD-C3-1 | 12 | 140 | C3 | P-104B |  |  |  |  | equipment.json (MCC hardwired interface)
P-105A XA | P-105A | Motor interface (MCC) | Overhead sour water P-105A - Motor fault / not available (5.5 kW) | P-105A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 3 | FAR-100/MC-CDU-2-D01 | TB02-5/6 | JB-DD-C3-1 | 29/30 | MC-DD-C3-1 | 15 | 140 | C3 | P-105A |  |  |  |  | equipment.json (MCC hardwired interface)
P-105A XL | P-105A | Motor interface (MCC) | Overhead sour water P-105A - Motor running (5.5 kW) | P-105A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 4 | FAR-100/MC-CDU-2-D01 | TB02-7/8 | JB-DD-C3-1 | 31/32 | MC-DD-C3-1 | 16 | 140 | C3 | P-105A |  |  |  |  | equipment.json (MCC hardwired interface)
P-105B XA | P-105B | Motor interface (MCC) | Overhead sour water P-105B - Motor fault / not available (5.5 kW) | P-105B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 5 | FAR-100/MC-CDU-2-D01 | TB02-9/10 | JB-DD-C3-1 | 37/38 | MC-DD-C3-1 | 19 | 150 | C3 | P-105B |  |  |  |  | equipment.json (MCC hardwired interface)
P-105B XL | P-105B | Motor interface (MCC) | Overhead sour water P-105B - Motor running (5.5 kW) | P-105B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 6 | FAR-100/MC-CDU-2-D01 | TB02-11/12 | JB-DD-C3-1 | 39/40 | MC-DD-C3-1 | 20 | 150 | C3 | P-105B |  |  |  |  | equipment.json (MCC hardwired interface)
P-108A XA | P-108A | Motor interface (MCC) | BPA pumparound P-108A - Motor fault / not available (132 kW) | P-108A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 7 | FAR-100/MC-CDU-2-D01 | TB02-13/14 | JB-DD-C3-1 | 45/46 | MC-DD-C3-1 | 23 | 160 | C3 | P-108A |  |  |  |  | equipment.json (MCC hardwired interface)
P-108A XL | P-108A | Motor interface (MCC) | BPA pumparound P-108A - Motor running (132 kW) | P-108A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 8 | FAR-100/MC-CDU-2-D01 | TB02-15/16 | JB-DD-C3-1 | 47/48 | MC-DD-C3-1 | 24 | 160 | C3 | P-108A |  |  |  |  | equipment.json (MCC hardwired interface)
P-108B XA | P-108B | Motor interface (MCC) | BPA pumparound P-108B - Motor fault / not available (132 kW) | P-108B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 9 | FAR-100/MC-CDU-2-D01 | TB02-17/18 | JB-DD-C3-2 | 5/6 | MC-DD-C3-2 | 3 | 160 | C3 | P-108B |  |  |  |  | equipment.json (MCC hardwired interface)
P-108B XL | P-108B | Motor interface (MCC) | BPA pumparound P-108B - Motor running (132 kW) | P-108B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 10 | FAR-100/MC-CDU-2-D01 | TB02-19/20 | JB-DD-C3-2 | 7/8 | MC-DD-C3-2 | 4 | 160 | C3 | P-108B |  |  |  |  | equipment.json (MCC hardwired interface)
P-109A XA | P-109A | Motor interface (MCC) | Kero product P-109A - Motor fault / not available (55 kW) | P-109A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 11 | FAR-100/MC-CDU-2-D01 | TB02-21/22 | JB-DD-C3-2 | 13/14 | MC-DD-C3-2 | 7 | 170 | C3 | P-109A |  |  |  |  | equipment.json (MCC hardwired interface)
P-109A XL | P-109A | Motor interface (MCC) | Kero product P-109A - Motor running (55 kW) | P-109A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 12 | FAR-100/MC-CDU-2-D01 | TB02-23/24 | JB-DD-C3-2 | 15/16 | MC-DD-C3-2 | 8 | 170 | C3 | P-109A |  |  |  |  | equipment.json (MCC hardwired interface)
P-109B XA | P-109B | Motor interface (MCC) | Kero product P-109B - Motor fault / not available (55 kW) | P-109B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 13 | FAR-100/MC-CDU-2-D01 | TB02-25/26 | JB-DD-C3-2 | 21/22 | MC-DD-C3-2 | 11 | 170 | C3 | P-109B |  |  |  |  | equipment.json (MCC hardwired interface)
P-109B XL | P-109B | Motor interface (MCC) | Kero product P-109B - Motor running (55 kW) | P-109B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 14 | FAR-100/MC-CDU-2-D01 | TB02-27/28 | JB-DD-C3-2 | 23/24 | MC-DD-C3-2 | 12 | 170 | C3 | P-109B |  |  |  |  | equipment.json (MCC hardwired interface)
P-110A XA | P-110A | Motor interface (MCC) | Diesel product P-110A - Motor fault / not available (75 kW) | P-110A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 15 | FAR-100/MC-CDU-2-D01 | TB02-29/30 | JB-DD-C3-2 | 29/30 | MC-DD-C3-2 | 15 | 170 | C3 | P-110A |  |  |  |  | equipment.json (MCC hardwired interface)
P-110A XL | P-110A | Motor interface (MCC) | Diesel product P-110A - Motor running (75 kW) | P-110A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 16 | FAR-100/MC-CDU-2-D01 | TB02-31/32 | JB-DD-C3-2 | 31/32 | MC-DD-C3-2 | 16 | 170 | C3 | P-110A |  |  |  |  | equipment.json (MCC hardwired interface)
P-110B XA | P-110B | Motor interface (MCC) | Diesel product P-110B - Motor fault / not available (75 kW) | P-110B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 17 | FAR-100/MC-CDU-2-D01 | TB02-33/34 | JB-DD-C3-2 | 37/38 | MC-DD-C3-2 | 19 | 180 | C3 | P-110B |  |  |  |  | equipment.json (MCC hardwired interface)
P-110B XL | P-110B | Motor interface (MCC) | Diesel product P-110B - Motor running (75 kW) | P-110B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 18 | FAR-100/MC-CDU-2-D01 | TB02-35/36 | JB-DD-C3-2 | 39/40 | MC-DD-C3-2 | 20 | 180 | C3 | P-110B |  |  |  |  | equipment.json (MCC hardwired interface)
P-111A XA | P-111A | Motor interface (MCC) | Ago product P-111A - Motor fault / not available (45 kW) | P-111A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 19 | FAR-100/MC-CDU-2-D01 | TB02-37/38 | JB-DD-C3-2 | 45/46 | MC-DD-C3-2 | 23 | 180 | C3 | P-111A |  |  |  |  | equipment.json (MCC hardwired interface)
P-111A XL | P-111A | Motor interface (MCC) | Ago product P-111A - Motor running (45 kW) | P-111A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 20 | FAR-100/MC-CDU-2-D01 | TB02-39/40 | JB-DD-C3-2 | 47/48 | MC-DD-C3-2 | 24 | 180 | C3 | P-111A |  |  |  |  | equipment.json (MCC hardwired interface)
P-112A XA | P-112A | Motor interface (MCC) | Atm. residue / vacuum heater charge P-112A - Motor fault / not available (315 kW) | P-112A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 21 | FAR-100/MC-CDU-2-D01 | TB02-41/42 | JB-DD-C3-3 | 5/6 | MC-DD-C3-3 | 3 | 150 | C3 | P-112A |  |  |  |  | equipment.json (MCC hardwired interface)
P-112A XL | P-112A | Motor interface (MCC) | Atm. residue / vacuum heater charge P-112A - Motor running (315 kW) | P-112A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 22 | FAR-100/MC-CDU-2-D01 | TB02-43/44 | JB-DD-C3-3 | 7/8 | MC-DD-C3-3 | 4 | 150 | C3 | P-112A |  |  |  |  | equipment.json (MCC hardwired interface)
P-112B XA | P-112B | Motor interface (MCC) | Atm. residue / vacuum heater charge P-112B - Motor fault / not available (315 kW) | P-112B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 23 | FAR-100/MC-CDU-2-D01 | TB02-45/46 | JB-DD-C3-3 | 13/14 | MC-DD-C3-3 | 7 | 160 | C3 | P-112B |  |  |  |  | equipment.json (MCC hardwired interface)
P-112B XL | P-112B | Motor interface (MCC) | Atm. residue / vacuum heater charge P-112B - Motor running (315 kW) | P-112B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 24 | FAR-100/MC-CDU-2-D01 | TB02-47/48 | JB-DD-C3-3 | 15/16 | MC-DD-C3-3 | 8 | 160 | C3 | P-112B |  |  |  |  | equipment.json (MCC hardwired interface)
A-101 XA | A-101 | Motor interface (MCC) | Atm. overhead condenser A-101 - Motor fault / not available (55 kW) | A-101 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 25 | FAR-100/MC-CDU-2-D01 | TB02-49/50 | JB-DD-C4 | 5/6 | MC-DD-C4 | 3 | 170 | C4 | A-101 |  |  |  |  | equipment.json (MCC hardwired interface)
A-101 XL | A-101 | Motor interface (MCC) | Atm. overhead condenser A-101 - Motor running (55 kW) | A-101 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI02 | 26 | FAR-100/MC-CDU-2-D01 | TB02-51/52 | JB-DD-C4 | 7/8 | MC-DD-C4 | 4 | 170 | C4 | A-101 |  |  |  |  | equipment.json (MCC hardwired interface)
A-107 XA | A-107 | Motor interface (MCC) | Splitter overhead condenser A-107 - Motor fault / not available (30 kW) | A-107 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 1 | FAR-100/MC-CDU-2-D01 | TB03-1/2 | JB-DD-C4 | 13/14 | MC-DD-C4 | 7 | 170 | C4 | A-107 |  |  |  |  | equipment.json (MCC hardwired interface)
A-107 XL | A-107 | Motor interface (MCC) | Splitter overhead condenser A-107 - Motor running (30 kW) | A-107 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 2 | FAR-100/MC-CDU-2-D01 | TB03-3/4 | JB-DD-C4 | 15/16 | MC-DD-C4 | 8 | 170 | C4 | A-107 |  |  |  |  | equipment.json (MCC hardwired interface)
XA-9101 | XA-9101 | Analyser house common alarm | AH-101 analyser house common trouble / HVAC | XA-9101 | (P&ID sheet 016) | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 3 | FAR-100/MC-CDU-2-D01 | TB03-5/6 | JB-DD-D1 | 3/4 | MC-DD-D1 | 2 | 140 | D1 | D-103 |  |  |  |  | I&C addition (add to index)
A-105 XA | A-105 | Motor interface (MCC) | Ago cooler A-105 - Motor fault / not available (30 kW) | A-105 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 4 | FAR-100/MC-CDU-2-D01 | TB03-7/8 | JB-DD-D3-1 | 5/6 | MC-DD-D3-1 | 3 | 180 | D3 | A-105 |  |  |  |  | equipment.json (MCC hardwired interface)
A-105 XL | A-105 | Motor interface (MCC) | Ago cooler A-105 - Motor running (30 kW) | A-105 |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 5 | FAR-100/MC-CDU-2-D01 | TB03-9/10 | JB-DD-D3-1 | 7/8 | MC-DD-D3-1 | 4 | 180 | D3 | A-105 |  |  |  |  | equipment.json (MCC hardwired interface)
P-106A XA | P-106A | Motor interface (MCC) | TPA pumparound P-106A - Motor fault / not available (110 kW) | P-106A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 6 | FAR-100/MC-CDU-2-D01 | TB03-11/12 | JB-DD-D3-1 | 21/22 | MC-DD-D3-1 | 11 | 190 | D3 | P-106A |  |  |  |  | equipment.json (MCC hardwired interface)
P-106A XL | P-106A | Motor interface (MCC) | TPA pumparound P-106A - Motor running (110 kW) | P-106A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 7 | FAR-100/MC-CDU-2-D01 | TB03-13/14 | JB-DD-D3-1 | 23/24 | MC-DD-D3-1 | 12 | 190 | D3 | P-106A |  |  |  |  | equipment.json (MCC hardwired interface)
P-106B XA | P-106B | Motor interface (MCC) | TPA pumparound P-106B - Motor fault / not available (110 kW) | P-106B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 8 | FAR-100/MC-CDU-2-D01 | TB03-15/16 | JB-DD-D3-1 | 29/30 | MC-DD-D3-1 | 15 | 190 | D3 | P-106B |  |  |  |  | equipment.json (MCC hardwired interface)
P-106B XL | P-106B | Motor interface (MCC) | TPA pumparound P-106B - Motor running (110 kW) | P-106B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 9 | FAR-100/MC-CDU-2-D01 | TB03-17/18 | JB-DD-D3-1 | 31/32 | MC-DD-D3-1 | 16 | 190 | D3 | P-106B |  |  |  |  | equipment.json (MCC hardwired interface)
P-107A XA | P-107A | Motor interface (MCC) | MPA pumparound P-107A - Motor fault / not available (160 kW) | P-107A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 10 | FAR-100/MC-CDU-2-D01 | TB03-19/20 | JB-DD-D3-1 | 37/38 | MC-DD-D3-1 | 19 | 200 | D3 | P-107A |  |  |  |  | equipment.json (MCC hardwired interface)
P-107A XL | P-107A | Motor interface (MCC) | MPA pumparound P-107A - Motor running (160 kW) | P-107A |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 11 | FAR-100/MC-CDU-2-D01 | TB03-21/22 | JB-DD-D3-1 | 39/40 | MC-DD-D3-1 | 20 | 200 | D3 | P-107A |  |  |  |  | equipment.json (MCC hardwired interface)
P-107B XA | P-107B | Motor interface (MCC) | MPA pumparound P-107B - Motor fault / not available (160 kW) | P-107B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 12 | FAR-100/MC-CDU-2-D01 | TB03-23/24 | JB-DD-D3-1 | 45/46 | MC-DD-D3-1 | 23 | 200 | D3 | P-107B |  |  |  |  | equipment.json (MCC hardwired interface)
P-107B XL | P-107B | Motor interface (MCC) | MPA pumparound P-107B - Motor running (160 kW) | P-107B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 13 | FAR-100/MC-CDU-2-D01 | TB03-25/26 | JB-DD-D3-1 | 47/48 | MC-DD-D3-1 | 24 | 200 | D3 | P-107B |  |  |  |  | equipment.json (MCC hardwired interface)
P-111B XA | P-111B | Motor interface (MCC) | Ago product P-111B - Motor fault / not available (45 kW) | P-111B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 14 | FAR-100/MC-CDU-2-D01 | TB03-27/28 | JB-DD-D3-2 | 5/6 | MC-DD-D3-2 | 3 | 190 | D3 | P-111B |  |  |  |  | equipment.json (MCC hardwired interface)
P-111B XL | P-111B | Motor interface (MCC) | Ago product P-111B - Motor running (45 kW) | P-111B |  | DCS | CDU-2 | DI | 24 VDC dry contact / NAMUR | CDU-2-DI03 | 15 | FAR-100/MC-CDU-2-D01 | TB03-29/30 | JB-DD-D3-2 | 7/8 | MC-DD-D3-2 | 4 | 190 | D3 | P-111B |  |  |  |  | equipment.json (MCC hardwired interface)
A-106 HS-START | A-106 | Motor interface (MCC) | Stabiliser overhead condenser A-106 - Start command (11 kW) | A-106 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 1 | FAR-100/MC-CDU-2-D01 | TB01-1/2 | JB-DD-B3-1 | 1/2 | MC-DD-B3-1 | 1 | 100 | B3 | A-106 |  |  |  |  | equipment.json (MCC hardwired interface)
A-106 HS-STOP | A-106 | Motor interface (MCC) | Stabiliser overhead condenser A-106 - Stop command (11 kW) | A-106 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 2 | FAR-100/MC-CDU-2-D01 | TB01-3/4 | JB-DD-B3-1 | 3/4 | MC-DD-B3-1 | 2 | 100 | B3 | A-106 |  |  |  |  | equipment.json (MCC hardwired interface)
A-108 HS-START | A-108 | Motor interface (MCC) | Heavy naphtha product cooler A-108 - Start command (30 kW) | A-108 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 3 | FAR-100/MC-CDU-2-D01 | TB01-5/6 | JB-DD-B3-1 | 9/10 | MC-DD-B3-1 | 5 | 110 | B3 | A-108 |  |  |  |  | equipment.json (MCC hardwired interface)
A-108 HS-STOP | A-108 | Motor interface (MCC) | Heavy naphtha product cooler A-108 - Stop command (30 kW) | A-108 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 4 | FAR-100/MC-CDU-2-D01 | TB01-7/8 | JB-DD-B3-1 | 11/12 | MC-DD-B3-1 | 6 | 110 | B3 | A-108 |  |  |  |  | equipment.json (MCC hardwired interface)
P-103A HS-START | P-103A | Motor interface (MCC) | Atm. reflux P-103A - Start command (55 kW) | P-103A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 5 | FAR-100/MC-CDU-2-D01 | TB01-9/10 | JB-DD-B3-1 | 33/34 | MC-DD-B3-1 | 17 | 130 | B3 | P-103A |  |  |  |  | equipment.json (MCC hardwired interface)
P-103A HS-STOP | P-103A | Motor interface (MCC) | Atm. reflux P-103A - Stop command (55 kW) | P-103A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 6 | FAR-100/MC-CDU-2-D01 | TB01-11/12 | JB-DD-B3-1 | 35/36 | MC-DD-B3-1 | 18 | 130 | B3 | P-103A |  |  |  |  | equipment.json (MCC hardwired interface)
P-103B HS-START | P-103B | Motor interface (MCC) | Atm. reflux P-103B - Start command (55 kW) | P-103B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 7 | FAR-100/MC-CDU-2-D01 | TB01-13/14 | JB-DD-B3-1 | 41/42 | MC-DD-B3-1 | 21 | 130 | B3 | P-103B |  |  |  |  | equipment.json (MCC hardwired interface)
P-103B HS-STOP | P-103B | Motor interface (MCC) | Atm. reflux P-103B - Stop command (55 kW) | P-103B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 8 | FAR-100/MC-CDU-2-D01 | TB01-15/16 | JB-DD-B3-1 | 43/44 | MC-DD-B3-1 | 22 | 130 | B3 | P-103B |  |  |  |  | equipment.json (MCC hardwired interface)
P-104A HS-START | P-104A | Motor interface (MCC) | Unstabilised naphtha P-104A - Start command (160 kW) | P-104A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 9 | FAR-100/MC-CDU-2-D01 | TB01-17/18 | JB-DD-B3-2 | 1/2 | MC-DD-B3-2 | 1 | 140 | B3 | P-104A |  |  |  |  | equipment.json (MCC hardwired interface)
P-104A HS-STOP | P-104A | Motor interface (MCC) | Unstabilised naphtha P-104A - Stop command (160 kW) | P-104A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 10 | FAR-100/MC-CDU-2-D01 | TB01-19/20 | JB-DD-B3-2 | 3/4 | MC-DD-B3-2 | 2 | 140 | B3 | P-104A |  |  |  |  | equipment.json (MCC hardwired interface)
P-115A HS-START | P-115A | Motor interface (MCC) | Stabiliser reflux / LPG P-115A - Start command (18.5 kW) | P-115A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 11 | FAR-100/MC-CDU-2-D01 | TB01-21/22 | JB-DD-B3-2 | 9/10 | MC-DD-B3-2 | 5 | 120 | B3 | P-115A |  |  |  |  | equipment.json (MCC hardwired interface)
P-115A HS-STOP | P-115A | Motor interface (MCC) | Stabiliser reflux / LPG P-115A - Stop command (18.5 kW) | P-115A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 12 | FAR-100/MC-CDU-2-D01 | TB01-23/24 | JB-DD-B3-2 | 11/12 | MC-DD-B3-2 | 6 | 120 | B3 | P-115A |  |  |  |  | equipment.json (MCC hardwired interface)
P-115B HS-START | P-115B | Motor interface (MCC) | Stabiliser reflux / LPG P-115B - Start command (18.5 kW) | P-115B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO01 | 13 | FAR-100/MC-CDU-2-D01 | TB01-25/26 | JB-DD-B3-2 | 17/18 | MC-DD-B3-2 | 9 | 120 | B3 | P-115B |  |  |  |  | equipment.json (MCC hardwired interface)
P-115B HS-STOP | P-115B | Motor interface (MCC) | Stabiliser reflux / LPG P-115B - Stop command (18.5 kW) | P-115B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 1 | FAR-100/MC-CDU-2-D01 | TB02-1/2 | JB-DD-B3-2 | 19/20 | MC-DD-B3-2 | 10 | 120 | B3 | P-115B |  |  |  |  | equipment.json (MCC hardwired interface)
P-116A HS-START | P-116A | Motor interface (MCC) | Splitter reflux / LN P-116A - Start command (55 kW) | P-116A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 2 | FAR-100/MC-CDU-2-D01 | TB02-3/4 | JB-DD-B3-2 | 25/26 | MC-DD-B3-2 | 13 | 110 | B3 | P-116A |  |  |  |  | equipment.json (MCC hardwired interface)
P-116A HS-STOP | P-116A | Motor interface (MCC) | Splitter reflux / LN P-116A - Stop command (55 kW) | P-116A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 3 | FAR-100/MC-CDU-2-D01 | TB02-5/6 | JB-DD-B3-2 | 27/28 | MC-DD-B3-2 | 14 | 110 | B3 | P-116A |  |  |  |  | equipment.json (MCC hardwired interface)
P-116B HS-START | P-116B | Motor interface (MCC) | Splitter reflux / LN P-116B - Start command (55 kW) | P-116B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 4 | FAR-100/MC-CDU-2-D01 | TB02-7/8 | JB-DD-B3-2 | 33/34 | MC-DD-B3-2 | 17 | 110 | B3 | P-116B |  |  |  |  | equipment.json (MCC hardwired interface)
P-116B HS-STOP | P-116B | Motor interface (MCC) | Splitter reflux / LN P-116B - Stop command (55 kW) | P-116B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 5 | FAR-100/MC-CDU-2-D01 | TB02-9/10 | JB-DD-B3-2 | 35/36 | MC-DD-B3-2 | 18 | 110 | B3 | P-116B |  |  |  |  | equipment.json (MCC hardwired interface)
P-117A HS-START | P-117A | Motor interface (MCC) | Heavy naphtha product P-117A - Start command (45 kW) | P-117A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 6 | FAR-100/MC-CDU-2-D01 | TB02-11/12 | JB-DD-B3-2 | 41/42 | MC-DD-B3-2 | 21 | 110 | B3 | P-117A |  |  |  |  | equipment.json (MCC hardwired interface)
P-117A HS-STOP | P-117A | Motor interface (MCC) | Heavy naphtha product P-117A - Stop command (45 kW) | P-117A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 7 | FAR-100/MC-CDU-2-D01 | TB02-13/14 | JB-DD-B3-2 | 43/44 | MC-DD-B3-2 | 22 | 110 | B3 | P-117A |  |  |  |  | equipment.json (MCC hardwired interface)
P-117B HS-START | P-117B | Motor interface (MCC) | Heavy naphtha product P-117B - Start command (45 kW) | P-117B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 8 | FAR-100/MC-CDU-2-D01 | TB02-15/16 | JB-DD-B3-3 | 1/2 | MC-DD-B3-3 | 1 | 110 | B3 | P-117B |  |  |  |  | equipment.json (MCC hardwired interface)
P-117B HS-STOP | P-117B | Motor interface (MCC) | Heavy naphtha product P-117B - Stop command (45 kW) | P-117B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 9 | FAR-100/MC-CDU-2-D01 | TB02-17/18 | JB-DD-B3-3 | 3/4 | MC-DD-B3-3 | 2 | 110 | B3 | P-117B |  |  |  |  | equipment.json (MCC hardwired interface)
A-103 HS-START | A-103 | Motor interface (MCC) | Kero cooler A-103 - Start command (11 kW) | A-103 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 10 | FAR-100/MC-CDU-2-D01 | TB02-19/20 | JB-DD-C3-1 | 1/2 | MC-DD-C3-1 | 1 | 160 | C3 | A-103 |  |  |  |  | equipment.json (MCC hardwired interface)
A-103 HS-STOP | A-103 | Motor interface (MCC) | Kero cooler A-103 - Stop command (11 kW) | A-103 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 11 | FAR-100/MC-CDU-2-D01 | TB02-21/22 | JB-DD-C3-1 | 3/4 | MC-DD-C3-1 | 2 | 160 | C3 | A-103 |  |  |  |  | equipment.json (MCC hardwired interface)
A-104 HS-START | A-104 | Motor interface (MCC) | Diesel cooler A-104 - Start command (18.5 kW) | A-104 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 12 | FAR-100/MC-CDU-2-D01 | TB02-23/24 | JB-DD-C3-1 | 9/10 | MC-DD-C3-1 | 5 | 170 | C3 | A-104 |  |  |  |  | equipment.json (MCC hardwired interface)
A-104 HS-STOP | A-104 | Motor interface (MCC) | Diesel cooler A-104 - Stop command (18.5 kW) | A-104 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO02 | 13 | FAR-100/MC-CDU-2-D01 | TB02-25/26 | JB-DD-C3-1 | 11/12 | MC-DD-C3-1 | 6 | 170 | C3 | A-104 |  |  |  |  | equipment.json (MCC hardwired interface)
P-104B HS-START | P-104B | Motor interface (MCC) | Unstabilised naphtha P-104B - Start command (160 kW) | P-104B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 1 | FAR-100/MC-CDU-2-D01 | TB03-1/2 | JB-DD-C3-1 | 17/18 | MC-DD-C3-1 | 9 | 140 | C3 | P-104B |  |  |  |  | equipment.json (MCC hardwired interface)
P-104B HS-STOP | P-104B | Motor interface (MCC) | Unstabilised naphtha P-104B - Stop command (160 kW) | P-104B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 2 | FAR-100/MC-CDU-2-D01 | TB03-3/4 | JB-DD-C3-1 | 19/20 | MC-DD-C3-1 | 10 | 140 | C3 | P-104B |  |  |  |  | equipment.json (MCC hardwired interface)
P-105A HS-START | P-105A | Motor interface (MCC) | Overhead sour water P-105A - Start command (5.5 kW) | P-105A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 3 | FAR-100/MC-CDU-2-D01 | TB03-5/6 | JB-DD-C3-1 | 25/26 | MC-DD-C3-1 | 13 | 140 | C3 | P-105A |  |  |  |  | equipment.json (MCC hardwired interface)
P-105A HS-STOP | P-105A | Motor interface (MCC) | Overhead sour water P-105A - Stop command (5.5 kW) | P-105A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 4 | FAR-100/MC-CDU-2-D01 | TB03-7/8 | JB-DD-C3-1 | 27/28 | MC-DD-C3-1 | 14 | 140 | C3 | P-105A |  |  |  |  | equipment.json (MCC hardwired interface)
P-105B HS-START | P-105B | Motor interface (MCC) | Overhead sour water P-105B - Start command (5.5 kW) | P-105B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 5 | FAR-100/MC-CDU-2-D01 | TB03-9/10 | JB-DD-C3-1 | 33/34 | MC-DD-C3-1 | 17 | 150 | C3 | P-105B |  |  |  |  | equipment.json (MCC hardwired interface)
P-105B HS-STOP | P-105B | Motor interface (MCC) | Overhead sour water P-105B - Stop command (5.5 kW) | P-105B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 6 | FAR-100/MC-CDU-2-D01 | TB03-11/12 | JB-DD-C3-1 | 35/36 | MC-DD-C3-1 | 18 | 150 | C3 | P-105B |  |  |  |  | equipment.json (MCC hardwired interface)
P-108A HS-START | P-108A | Motor interface (MCC) | BPA pumparound P-108A - Start command (132 kW) | P-108A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 7 | FAR-100/MC-CDU-2-D01 | TB03-13/14 | JB-DD-C3-1 | 41/42 | MC-DD-C3-1 | 21 | 160 | C3 | P-108A |  |  |  |  | equipment.json (MCC hardwired interface)
P-108A HS-STOP | P-108A | Motor interface (MCC) | BPA pumparound P-108A - Stop command (132 kW) | P-108A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 8 | FAR-100/MC-CDU-2-D01 | TB03-15/16 | JB-DD-C3-1 | 43/44 | MC-DD-C3-1 | 22 | 160 | C3 | P-108A |  |  |  |  | equipment.json (MCC hardwired interface)
P-108B HS-START | P-108B | Motor interface (MCC) | BPA pumparound P-108B - Start command (132 kW) | P-108B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 9 | FAR-100/MC-CDU-2-D01 | TB03-17/18 | JB-DD-C3-2 | 1/2 | MC-DD-C3-2 | 1 | 160 | C3 | P-108B |  |  |  |  | equipment.json (MCC hardwired interface)
P-108B HS-STOP | P-108B | Motor interface (MCC) | BPA pumparound P-108B - Stop command (132 kW) | P-108B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 10 | FAR-100/MC-CDU-2-D01 | TB03-19/20 | JB-DD-C3-2 | 3/4 | MC-DD-C3-2 | 2 | 160 | C3 | P-108B |  |  |  |  | equipment.json (MCC hardwired interface)
P-109A HS-START | P-109A | Motor interface (MCC) | Kero product P-109A - Start command (55 kW) | P-109A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 11 | FAR-100/MC-CDU-2-D01 | TB03-21/22 | JB-DD-C3-2 | 9/10 | MC-DD-C3-2 | 5 | 170 | C3 | P-109A |  |  |  |  | equipment.json (MCC hardwired interface)
P-109A HS-STOP | P-109A | Motor interface (MCC) | Kero product P-109A - Stop command (55 kW) | P-109A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 12 | FAR-100/MC-CDU-2-D01 | TB03-23/24 | JB-DD-C3-2 | 11/12 | MC-DD-C3-2 | 6 | 170 | C3 | P-109A |  |  |  |  | equipment.json (MCC hardwired interface)
P-109B HS-START | P-109B | Motor interface (MCC) | Kero product P-109B - Start command (55 kW) | P-109B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO03 | 13 | FAR-100/MC-CDU-2-D01 | TB03-25/26 | JB-DD-C3-2 | 17/18 | MC-DD-C3-2 | 9 | 170 | C3 | P-109B |  |  |  |  | equipment.json (MCC hardwired interface)
P-109B HS-STOP | P-109B | Motor interface (MCC) | Kero product P-109B - Stop command (55 kW) | P-109B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 1 | FAR-100/MC-CDU-2-D01 | TB04-1/2 | JB-DD-C3-2 | 19/20 | MC-DD-C3-2 | 10 | 170 | C3 | P-109B |  |  |  |  | equipment.json (MCC hardwired interface)
P-110A HS-START | P-110A | Motor interface (MCC) | Diesel product P-110A - Start command (75 kW) | P-110A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 2 | FAR-100/MC-CDU-2-D01 | TB04-3/4 | JB-DD-C3-2 | 25/26 | MC-DD-C3-2 | 13 | 170 | C3 | P-110A |  |  |  |  | equipment.json (MCC hardwired interface)
P-110A HS-STOP | P-110A | Motor interface (MCC) | Diesel product P-110A - Stop command (75 kW) | P-110A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 3 | FAR-100/MC-CDU-2-D01 | TB04-5/6 | JB-DD-C3-2 | 27/28 | MC-DD-C3-2 | 14 | 170 | C3 | P-110A |  |  |  |  | equipment.json (MCC hardwired interface)
P-110B HS-START | P-110B | Motor interface (MCC) | Diesel product P-110B - Start command (75 kW) | P-110B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 4 | FAR-100/MC-CDU-2-D01 | TB04-7/8 | JB-DD-C3-2 | 33/34 | MC-DD-C3-2 | 17 | 180 | C3 | P-110B |  |  |  |  | equipment.json (MCC hardwired interface)
P-110B HS-STOP | P-110B | Motor interface (MCC) | Diesel product P-110B - Stop command (75 kW) | P-110B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 5 | FAR-100/MC-CDU-2-D01 | TB04-9/10 | JB-DD-C3-2 | 35/36 | MC-DD-C3-2 | 18 | 180 | C3 | P-110B |  |  |  |  | equipment.json (MCC hardwired interface)
P-111A HS-START | P-111A | Motor interface (MCC) | Ago product P-111A - Start command (45 kW) | P-111A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 6 | FAR-100/MC-CDU-2-D01 | TB04-11/12 | JB-DD-C3-2 | 41/42 | MC-DD-C3-2 | 21 | 180 | C3 | P-111A |  |  |  |  | equipment.json (MCC hardwired interface)
P-111A HS-STOP | P-111A | Motor interface (MCC) | Ago product P-111A - Stop command (45 kW) | P-111A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 7 | FAR-100/MC-CDU-2-D01 | TB04-13/14 | JB-DD-C3-2 | 43/44 | MC-DD-C3-2 | 22 | 180 | C3 | P-111A |  |  |  |  | equipment.json (MCC hardwired interface)
P-112A HS-START | P-112A | Motor interface (MCC) | Atm. residue / vacuum heater charge P-112A - Start command (315 kW) | P-112A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 8 | FAR-100/MC-CDU-2-D01 | TB04-15/16 | JB-DD-C3-3 | 1/2 | MC-DD-C3-3 | 1 | 150 | C3 | P-112A |  |  |  |  | equipment.json (MCC hardwired interface)
P-112A HS-STOP | P-112A | Motor interface (MCC) | Atm. residue / vacuum heater charge P-112A - Stop command (315 kW) | P-112A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 9 | FAR-100/MC-CDU-2-D01 | TB04-17/18 | JB-DD-C3-3 | 3/4 | MC-DD-C3-3 | 2 | 150 | C3 | P-112A |  |  |  |  | equipment.json (MCC hardwired interface)
P-112B HS-START | P-112B | Motor interface (MCC) | Atm. residue / vacuum heater charge P-112B - Start command (315 kW) | P-112B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 10 | FAR-100/MC-CDU-2-D01 | TB04-19/20 | JB-DD-C3-3 | 9/10 | MC-DD-C3-3 | 5 | 160 | C3 | P-112B |  |  |  |  | equipment.json (MCC hardwired interface)
P-112B HS-STOP | P-112B | Motor interface (MCC) | Atm. residue / vacuum heater charge P-112B - Stop command (315 kW) | P-112B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 11 | FAR-100/MC-CDU-2-D01 | TB04-21/22 | JB-DD-C3-3 | 11/12 | MC-DD-C3-3 | 6 | 160 | C3 | P-112B |  |  |  |  | equipment.json (MCC hardwired interface)
A-101 HS-START | A-101 | Motor interface (MCC) | Atm. overhead condenser A-101 - Start command (55 kW) | A-101 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 12 | FAR-100/MC-CDU-2-D01 | TB04-23/24 | JB-DD-C4 | 1/2 | MC-DD-C4 | 1 | 170 | C4 | A-101 |  |  |  |  | equipment.json (MCC hardwired interface)
A-101 HS-STOP | A-101 | Motor interface (MCC) | Atm. overhead condenser A-101 - Stop command (55 kW) | A-101 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO04 | 13 | FAR-100/MC-CDU-2-D01 | TB04-25/26 | JB-DD-C4 | 3/4 | MC-DD-C4 | 2 | 170 | C4 | A-101 |  |  |  |  | equipment.json (MCC hardwired interface)
A-107 HS-START | A-107 | Motor interface (MCC) | Splitter overhead condenser A-107 - Start command (30 kW) | A-107 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 1 | FAR-100/MC-CDU-2-D01 | TB05-1/2 | JB-DD-C4 | 9/10 | MC-DD-C4 | 5 | 170 | C4 | A-107 |  |  |  |  | equipment.json (MCC hardwired interface)
A-107 HS-STOP | A-107 | Motor interface (MCC) | Splitter overhead condenser A-107 - Stop command (30 kW) | A-107 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 2 | FAR-100/MC-CDU-2-D01 | TB05-3/4 | JB-DD-C4 | 11/12 | MC-DD-C4 | 6 | 170 | C4 | A-107 |  |  |  |  | equipment.json (MCC hardwired interface)
A-105 HS-START | A-105 | Motor interface (MCC) | Ago cooler A-105 - Start command (30 kW) | A-105 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 3 | FAR-100/MC-CDU-2-D01 | TB05-5/6 | JB-DD-D3-1 | 1/2 | MC-DD-D3-1 | 1 | 180 | D3 | A-105 |  |  |  |  | equipment.json (MCC hardwired interface)
A-105 HS-STOP | A-105 | Motor interface (MCC) | Ago cooler A-105 - Stop command (30 kW) | A-105 |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 4 | FAR-100/MC-CDU-2-D01 | TB05-7/8 | JB-DD-D3-1 | 3/4 | MC-DD-D3-1 | 2 | 180 | D3 | A-105 |  |  |  |  | equipment.json (MCC hardwired interface)
P-106A HS-START | P-106A | Motor interface (MCC) | TPA pumparound P-106A - Start command (110 kW) | P-106A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 5 | FAR-100/MC-CDU-2-D01 | TB05-9/10 | JB-DD-D3-1 | 17/18 | MC-DD-D3-1 | 9 | 190 | D3 | P-106A |  |  |  |  | equipment.json (MCC hardwired interface)
P-106A HS-STOP | P-106A | Motor interface (MCC) | TPA pumparound P-106A - Stop command (110 kW) | P-106A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 6 | FAR-100/MC-CDU-2-D01 | TB05-11/12 | JB-DD-D3-1 | 19/20 | MC-DD-D3-1 | 10 | 190 | D3 | P-106A |  |  |  |  | equipment.json (MCC hardwired interface)
P-106B HS-START | P-106B | Motor interface (MCC) | TPA pumparound P-106B - Start command (110 kW) | P-106B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 7 | FAR-100/MC-CDU-2-D01 | TB05-13/14 | JB-DD-D3-1 | 25/26 | MC-DD-D3-1 | 13 | 190 | D3 | P-106B |  |  |  |  | equipment.json (MCC hardwired interface)
P-106B HS-STOP | P-106B | Motor interface (MCC) | TPA pumparound P-106B - Stop command (110 kW) | P-106B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 8 | FAR-100/MC-CDU-2-D01 | TB05-15/16 | JB-DD-D3-1 | 27/28 | MC-DD-D3-1 | 14 | 190 | D3 | P-106B |  |  |  |  | equipment.json (MCC hardwired interface)
P-107A HS-START | P-107A | Motor interface (MCC) | MPA pumparound P-107A - Start command (160 kW) | P-107A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 9 | FAR-100/MC-CDU-2-D01 | TB05-17/18 | JB-DD-D3-1 | 33/34 | MC-DD-D3-1 | 17 | 200 | D3 | P-107A |  |  |  |  | equipment.json (MCC hardwired interface)
P-107A HS-STOP | P-107A | Motor interface (MCC) | MPA pumparound P-107A - Stop command (160 kW) | P-107A |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 10 | FAR-100/MC-CDU-2-D01 | TB05-19/20 | JB-DD-D3-1 | 35/36 | MC-DD-D3-1 | 18 | 200 | D3 | P-107A |  |  |  |  | equipment.json (MCC hardwired interface)
P-107B HS-START | P-107B | Motor interface (MCC) | MPA pumparound P-107B - Start command (160 kW) | P-107B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 11 | FAR-100/MC-CDU-2-D01 | TB05-21/22 | JB-DD-D3-1 | 41/42 | MC-DD-D3-1 | 21 | 200 | D3 | P-107B |  |  |  |  | equipment.json (MCC hardwired interface)
P-107B HS-STOP | P-107B | Motor interface (MCC) | MPA pumparound P-107B - Stop command (160 kW) | P-107B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 12 | FAR-100/MC-CDU-2-D01 | TB05-23/24 | JB-DD-D3-1 | 43/44 | MC-DD-D3-1 | 22 | 200 | D3 | P-107B |  |  |  |  | equipment.json (MCC hardwired interface)
P-111B HS-START | P-111B | Motor interface (MCC) | Ago product P-111B - Start command (45 kW) | P-111B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO05 | 13 | FAR-100/MC-CDU-2-D01 | TB05-25/26 | JB-DD-D3-2 | 1/2 | MC-DD-D3-2 | 1 | 190 | D3 | P-111B |  |  |  |  | equipment.json (MCC hardwired interface)
P-111B HS-STOP | P-111B | Motor interface (MCC) | Ago product P-111B - Stop command (45 kW) | P-111B |  | DCS | CDU-2 | DO | 24 VDC interposing relay | CDU-2-DO06 | 1 | FAR-100/MC-CDU-2-D01 | TB06-1/2 | JB-DD-D3-2 | 3/4 | MC-DD-D3-2 | 2 | 190 | D3 | P-111B |  |  |  |  | equipment.json (MCC hardwired interface)
LT-2030 | LT-2030 | Level transmitter | E-201 steam-generator level | LIC-2030 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 1 | FAR-100/MC-VDU-A01 | TB01-1/2 | JB-DA-B4-2 | 7/8 | MC-DA-B4-2 | 4 | 150 | B4 | E-201 |  |  | 0-100 | % | instrument index
AT-2008 | AT-2008 | Analyser transmitter | H-201 flue gas O2 analyser | AIC-2008 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 2 | FAR-100/MC-VDU-A01 | TB01-3/4 | JB-DA-E2-1 | 1/2 | MC-DA-E2-1 | 1 | 190 | E2 | H-201 |  |  | 0-10 | vol% O2 | instrument index
FT-2001 | FT-2001 | Flow transmitter | H-201 pass 1 flow | FIC-2001 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 3 | FAR-100/MC-VDU-A01 | TB01-5/6 | JB-DA-E2-1 | 7/8 | MC-DA-E2-1 | 4 | 190 | E2 | H-201 |  |  | 0-120 | m3/h | instrument index
FT-2002 | FT-2002 | Flow transmitter | H-201 pass 2 flow | FIC-2002 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 4 | FAR-100/MC-VDU-A01 | TB01-7/8 | JB-DA-E2-1 | 9/10 | MC-DA-E2-1 | 5 | 190 | E2 | H-201 |  |  | 0-120 | m3/h | instrument index
FT-2003 | FT-2003 | Flow transmitter | H-201 pass 3 flow | FIC-2003 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 5 | FAR-100/MC-VDU-A01 | TB01-9/10 | JB-DA-E2-1 | 11/12 | MC-DA-E2-1 | 6 | 190 | E2 | H-201 |  |  | 0-120 | m3/h | instrument index
FT-2004 | FT-2004 | Flow transmitter | H-201 pass 4 flow | FIC-2004 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 6 | FAR-100/MC-VDU-A01 | TB01-11/12 | JB-DA-E2-1 | 13/14 | MC-DA-E2-1 | 7 | 190 | E2 | H-201 |  |  | 0-120 | m3/h | instrument index
FT-2006 | FT-2006 | Flow transmitter | H-201 fuel gas flow (cross-limiting fuel measurement) | PIC-2006 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 7 | FAR-100/MC-VDU-A01 | TB01-13/14 | JB-DA-E2-1 | 15/16 | MC-DA-E2-1 | 8 | 190 | E2 | H-201 |  |  | 0-2000 | kg/h | instrument index
FT-2006 | FT-2006 | Flow transmitter | H-201 fuel gas flow (cross-limiting fuel measurement) | FT-2006 | (P&ID sheet 012) | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 8 | FAR-100/MC-VDU-A01 | TB01-15/16 | JB-DA-E2-1 | 17/18 | MC-DA-E2-1 | 9 | 190 | E2 | H-201 |  |  |  |  | I&C addition (add to index)
FT-2007 | FT-2007 | Flow transmitter | H-201 coil (velocity) steam | FIC-2007 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 9 | FAR-100/MC-VDU-A01 | TB01-17/18 | JB-DA-E2-1 | 19/20 | MC-DA-E2-1 | 10 | 190 | E2 | H-201 |  |  | 0-1500 | kg/h | instrument index
PT-2006 | PT-2006 | Pressure transmitter | H-201 fuel gas pressure | PIC-2006 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 10 | FAR-100/MC-VDU-A01 | TB01-19/20 | JB-DA-E2-1 | 33/34 | MC-DA-E2-1 | 17 | 190 | E2 | H-201 |  |  | 0-6 | barg | instrument index
PT-2031 | PT-2031 | Pressure transmitter | Vacuum off-gas to H-201 | PIC-2031 | CFU-200-PR-PID-015 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 11 | FAR-100/MC-VDU-A01 | TB01-21/22 | JB-DA-E2-1 | 35/36 | MC-DA-E2-1 | 18 | 190 | E2 | H-201 |  |  | 0-2.5 | barg | instrument index
TI-2100 | TI-2100 | Temperature indicator | H-201 pass 1 outlet temperature | TI-2100 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 12 | FAR-100/MC-VDU-A01 | TB01-23/24 | JB-DA-E2-1 | 43/44 | MC-DA-E2-1 | 22 | 190 | E2 | H-201 |  |  | 0-600 | C | instrument index
TI-2101 | TI-2101 | Temperature indicator | H-201 pass 2 outlet temperature | TI-2101 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI01 | 13 | FAR-100/MC-VDU-A01 | TB01-25/26 | JB-DA-E2-1 | 45/46 | MC-DA-E2-1 | 23 | 190 | E2 | H-201 |  |  | 0-600 | C | instrument index
TI-2102 | TI-2102 | Temperature indicator | H-201 pass 3 outlet temperature | TI-2102 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 1 | FAR-100/MC-VDU-A01 | TB02-1/2 | JB-DA-E2-1 | 47/48 | MC-DA-E2-1 | 24 | 190 | E2 | H-201 |  |  | 0-600 | C | instrument index
TI-2103 | TI-2103 | Temperature indicator | H-201 pass 4 outlet temperature | TI-2103 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 2 | FAR-100/MC-VDU-A01 | TB02-3/4 | JB-DA-E2-2 | 1/2 | MC-DA-E2-2 | 1 | 190 | E2 | H-201 |  |  | 0-600 | C | instrument index
TT-2005 | TT-2005 | Temperature transmitter | H-201 COT | TIC-2005 | CFU-200-PR-PID-012 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 3 | FAR-100/MC-VDU-A01 | TB02-5/6 | JB-DA-E2-2 | 3/4 | MC-DA-E2-2 | 2 | 190 | E2 | H-201 |  |  | 0-600 | C | instrument index
FT-2011 | FT-2011 | Flow transmitter | LVGO PA circulation | FIC-2011 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 4 | FAR-100/MC-VDU-A01 | TB02-7/8 | JB-DA-E3 | 1/2 | MC-DA-E3 | 1 | 270 | E3 | P-201A |  |  | 0-150 | m3/h | instrument index
FT-2015 | FT-2015 | Flow transmitter | LVGO product | FIC-2015 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 5 | FAR-100/MC-VDU-A01 | TB02-9/10 | JB-DA-E3 | 3/4 | MC-DA-E3 | 2 | 270 | E3 | P-201A |  |  | 0-80 | m3/h | instrument index
FT-2016 | FT-2016 | Flow transmitter | HVGO PA circulation | FIC-2016 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 6 | FAR-100/MC-VDU-A01 | TB02-11/12 | JB-DA-E3 | 5/6 | MC-DA-E3 | 3 | 260 | E3 | P-202A |  |  | 0-300 | m3/h | instrument index
FT-2019 | FT-2019 | Flow transmitter | HVGO product | FIC-2019 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 7 | FAR-100/MC-VDU-A01 | TB02-13/14 | JB-DA-E3 | 7/8 | MC-DA-E3 | 4 | 260 | E3 | P-202A |  |  | 0-150 | m3/h | instrument index
FT-2022 | FT-2022 | Flow transmitter | Slop wax product | FIC-2022 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 8 | FAR-100/MC-VDU-A01 | TB02-15/16 | JB-DA-E3 | 9/10 | MC-DA-E3 | 5 | 260 | E3 | P-203A |  |  | 0-15 | m3/h | instrument index
FT-2025 | FT-2025 | Flow transmitter | Vacuum residue product | FIC-2025 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 9 | FAR-100/MC-VDU-A01 | TB02-17/18 | JB-DA-E3 | 11/12 | MC-DA-E3 | 6 | 250 | E3 | P-204A |  |  | 0-200 | m3/h | instrument index
AT-2032 | AT-2032 | Analyser transmitter | Vacuum off-gas H2S (D-202, to H-201 firing / SO2 emissions) | AT-2032 | (P&ID sheet 015) | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 10 | FAR-100/MC-VDU-A01 | TB02-19/20 | JB-DA-E4-1 | 1/2 | MC-DA-E4-1 | 1 | 300 | E4 | D-201 |  |  |  |  | I&C addition (add to index)
FT-2020 | FT-2020 | Flow transmitter | Wash oil to wash bed (critical, min-flow) | FIC-2020 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 11 | FAR-100/MC-VDU-A01 | TB02-21/22 | JB-DA-E4-1 | 3/4 | MC-DA-E4-1 | 2 | 270 | E4 | C-201 |  |  | 0-25 | m3/h | instrument index
FT-2023 | FT-2023 | Flow transmitter | C-201 bottom stripping steam | FIC-2023 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 12 | FAR-100/MC-VDU-A01 | TB02-23/24 | JB-DA-E4-1 | 5/6 | MC-DA-E4-1 | 3 | 270 | E4 | C-201 |  |  | 0-4000 | kg/h | instrument index
FT-2027 | FT-2027 | Flow transmitter | VR quench flow | FIC-2027 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI02 | 13 | FAR-100/MC-VDU-A01 | TB02-25/26 | JB-DA-E4-1 | 7/8 | MC-DA-E4-1 | 4 | 270 | E4 | C-201 |  |  | 0-40 | m3/h | instrument index
LT-2014 | LT-2014 | Level transmitter | LVGO draw-pan level | LIC-2014 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 1 | FAR-100/MC-VDU-A01 | TB03-1/2 | JB-DA-E4-1 | 15/16 | MC-DA-E4-1 | 8 | 270 | E4 | C-201 |  |  | 0-100 | % | instrument index
LT-2018 | LT-2018 | Level transmitter | HVGO draw-pan level | LIC-2018 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 2 | FAR-100/MC-VDU-A01 | TB03-3/4 | JB-DA-E4-1 | 17/18 | MC-DA-E4-1 | 9 | 270 | E4 | C-201 |  |  | 0-100 | % | instrument index
LT-2021 | LT-2021 | Level transmitter | Slop-wax pan level | LIC-2021 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 3 | FAR-100/MC-VDU-A01 | TB03-5/6 | JB-DA-E4-1 | 19/20 | MC-DA-E4-1 | 10 | 270 | E4 | C-201 |  |  | 0-100 | % | instrument index
LT-2024 | LT-2024 | Level transmitter | C-201 bottom level | LIC-2024 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 4 | FAR-100/MC-VDU-A01 | TB03-7/8 | JB-DA-E4-1 | 21/22 | MC-DA-E4-1 | 11 | 270 | E4 | C-201 |  |  | 0-100 | % | instrument index
LT-2028 | LT-2028 | Level transmitter | D-201 hotwell water level | LIC-2028 | CFU-200-PR-PID-015 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 5 | FAR-100/MC-VDU-A01 | TB03-9/10 | JB-DA-E4-1 | 23/24 | MC-DA-E4-1 | 12 | 300 | E4 | D-201 |  |  | 0-100 | % | instrument index
LT-2029 | LT-2029 | Level transmitter | D-201 slop oil level | LIC-2029 | CFU-200-PR-PID-015 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 6 | FAR-100/MC-VDU-A01 | TB03-11/12 | JB-DA-E4-1 | 25/26 | MC-DA-E4-1 | 13 | 300 | E4 | D-201 |  |  | 0-100 | % | instrument index
PDI-2108 | PDI-2108 | Differential pressure indicator | C-201 dP top - flash zone | PDI-2108 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 7 | FAR-100/MC-VDU-A01 | TB03-13/14 | JB-DA-E4-1 | 31/32 | MC-DA-E4-1 | 16 | 270 | E4 | C-201 |  |  | 0-2.5 | bar | instrument index
PT-2010 | PT-2010 | Pressure transmitter | C-201 top pressure (vacuum) | PIC-2010 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 8 | FAR-100/MC-VDU-A01 | TB03-15/16 | JB-DA-E4-1 | 33/34 | MC-DA-E4-1 | 17 | 270 | E4 | C-201 |  |  | 0-1100 | mbar(a) | instrument index
TI-2107 | TI-2107 | Temperature indicator | C-201 flash zone temperature | TI-2107 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 9 | FAR-100/MC-VDU-A01 | TB03-17/18 | JB-DA-E4-1 | 37/38 | MC-DA-E4-1 | 19 | 270 | E4 | C-201 |  |  | 0-600 | C | instrument index
TI-2109 | TI-2109 | Temperature indicator | LVGO draw temperature | TI-2109 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 10 | FAR-100/MC-VDU-A01 | TB03-19/20 | JB-DA-E4-1 | 39/40 | MC-DA-E4-1 | 20 | 270 | E4 | C-201 |  |  | 0-300 | C | instrument index
TI-2110 | TI-2110 | Temperature indicator | HVGO draw temperature | TI-2110 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 11 | FAR-100/MC-VDU-A01 | TB03-21/22 | JB-DA-E4-1 | 41/42 | MC-DA-E4-1 | 21 | 270 | E4 | C-201 |  |  | 0-500 | C | instrument index
TI-2111 | TI-2111 | Temperature indicator | SLOP draw temperature | TI-2111 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 12 | FAR-100/MC-VDU-A01 | TB03-23/24 | JB-DA-E4-1 | 43/44 | MC-DA-E4-1 | 22 | 270 | E4 | C-201 |  |  | 0-500 | C | instrument index
TI-2116 | TI-2116 | Temperature indicator | LVGO product temperature | TI-2116 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI03 | 13 | FAR-100/MC-VDU-A01 | TB03-25/26 | JB-DA-E4-1 | 45/46 | MC-DA-E4-1 | 23 | 270 | E4 | C-201 |  |  | 0-120 | C | instrument index
TI-2122 | TI-2122 | Temperature indicator | E-202 vapour outlet temperature | TI-2122 | CFU-200-PR-PID-015 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI04 | 1 | FAR-100/MC-VDU-A01 | TB04-1/2 | JB-DA-E4-1 | 47/48 | MC-DA-E4-1 | 24 | 290 | E4 | E-202 |  |  | 0-400 | C | instrument index
TI-2124 | TI-2124 | Temperature indicator | E-203 vapour outlet temperature | TI-2124 | CFU-200-PR-PID-015 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI04 | 2 | FAR-100/MC-VDU-A01 | TB04-3/4 | JB-DA-E4-2 | 1/2 | MC-DA-E4-2 | 1 | 290 | E4 | E-203 |  |  | 0-400 | C | instrument index
TI-2126 | TI-2126 | Temperature indicator | E-204 vapour outlet temperature | TI-2126 | CFU-200-PR-PID-015 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI04 | 3 | FAR-100/MC-VDU-A01 | TB04-5/6 | JB-DA-E4-2 | 3/4 | MC-DA-E4-2 | 2 | 290 | E4 | E-204 |  |  | 0-400 | C | instrument index
TT-2012 | TT-2012 | Temperature transmitter | C-201 top temperature | TIC-2012 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI04 | 4 | FAR-100/MC-VDU-A01 | TB04-7/8 | JB-DA-E4-2 | 5/6 | MC-DA-E4-2 | 3 | 270 | E4 | C-201 |  |  | 0-120 | C | instrument index
TT-2013 | TT-2013 | Temperature transmitter | LVGO PA return temperature | TIC-2013 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI04 | 5 | FAR-100/MC-VDU-A01 | TB04-9/10 | JB-DA-E4-2 | 7/8 | MC-DA-E4-2 | 4 | 270 | E4 | C-201 |  |  | 0-120 | C | instrument index
TT-2017 | TT-2017 | Temperature transmitter | HVGO PA return temperature | TIC-2017 | CFU-200-PR-PID-014 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI04 | 6 | FAR-100/MC-VDU-A01 | TB04-11/12 | JB-DA-E4-2 | 9/10 | MC-DA-E4-2 | 5 | 270 | E4 | C-201 |  |  | 0-300 | C | instrument index
TT-2026 | TT-2026 | Temperature transmitter | C-201 bottoms temperature (coking control) | TIC-2026 | CFU-200-PR-PID-013 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI04 | 7 | FAR-100/MC-VDU-A01 | TB04-13/14 | JB-DA-E4-2 | 11/12 | MC-DA-E4-2 | 6 | 270 | E4 | C-201 |  |  | 0-500 | C | instrument index
AT-2032 | AT-2032 | Analyser transmitter | Vacuum off-gas H2S analyser (D-202 outlet, H-201 firing / SO2) | AT-2032 | CFU-200-PR-PID-015 | DCS | VDU | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | VDU-AI04 | 8 | FAR-100/MC-VDU-A01 | TB04-15/16 | JB-DA-F4 | 1/2 | MC-DA-F4 | 1 | 310 | F4 | D-202 |  |  | 0-10 | mol% H2S | instrument index
LV-2030 | LV-2030 | Level control valve | E-201 steam-generator level - Valve positioner / output | LIC-2030 | CFU-200-PR-PID-014 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO01 | 1 | FAR-100/MC-VDU-A01 | TB01-1/2 | JB-DA-B4-2 | 17/18 | MC-DA-B4-2 | 9 | 150 | B4 | E-201 |  |  |  |  | instrument index
TY-2013 | TY-2013 | Temperature relay / output signal | A-201 fan auto-variable pitch signal - Valve positioner / output | TIC-2013 | CFU-200-PR-PID-014 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO01 | 2 | FAR-100/MC-VDU-A01 | TB01-3/4 | JB-DA-D3 | 9/10 | MC-DA-D3 | 5 | 220 | D3 | A-201 |  |  |  |  | instrument index
AV-2008 | AV-2008 | Analyser control element (damper/vane) | H-201 stack damper actuator (AIC-2008) - Valve positioner / output | AIC-2008 | CFU-200-PR-PID-012 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO01 | 3 | FAR-100/MC-VDU-A01 | TB01-5/6 | JB-DA-E2-1 | 3/4 | MC-DA-E2-1 | 2 | 190 | E2 | H-201 |  |  |  |  | instrument index
FV-2001 | FV-2001 | Flow control valve | H-201 pass 1 flow - Valve positioner / output | FIC-2001 | CFU-200-PR-PID-012 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO01 | 4 | FAR-100/MC-VDU-A01 | TB01-7/8 | JB-DA-E2-1 | 23/24 | MC-DA-E2-1 | 12 | 190 | E2 | H-201 |  |  |  |  | instrument index
FV-2002 | FV-2002 | Flow control valve | H-201 pass 2 flow - Valve positioner / output | FIC-2002 | CFU-200-PR-PID-012 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO01 | 5 | FAR-100/MC-VDU-A01 | TB01-9/10 | JB-DA-E2-1 | 25/26 | MC-DA-E2-1 | 13 | 190 | E2 | H-201 |  |  |  |  | instrument index
FV-2003 | FV-2003 | Flow control valve | H-201 pass 3 flow - Valve positioner / output | FIC-2003 | CFU-200-PR-PID-012 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO01 | 6 | FAR-100/MC-VDU-A01 | TB01-11/12 | JB-DA-E2-1 | 27/28 | MC-DA-E2-1 | 14 | 190 | E2 | H-201 |  |  |  |  | instrument index
FV-2004 | FV-2004 | Flow control valve | H-201 pass 4 flow - Valve positioner / output | FIC-2004 | CFU-200-PR-PID-012 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO02 | 1 | FAR-100/MC-VDU-A01 | TB02-1/2 | JB-DA-E2-1 | 29/30 | MC-DA-E2-1 | 15 | 190 | E2 | H-201 |  |  |  |  | instrument index
FV-2007 | FV-2007 | Flow control valve | H-201 coil (velocity) steam - Valve positioner / output | FIC-2007 | CFU-200-PR-PID-012 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO02 | 2 | FAR-100/MC-VDU-A01 | TB02-3/4 | JB-DA-E2-1 | 31/32 | MC-DA-E2-1 | 16 | 190 | E2 | H-201 |  |  |  |  | instrument index
PV-2006 | PV-2006 | Pressure control valve | H-201 fuel gas pressure - Valve positioner / output | PIC-2006 | CFU-200-PR-PID-012 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO02 | 3 | FAR-100/MC-VDU-A01 | TB02-5/6 | JB-DA-E2-1 | 37/38 | MC-DA-E2-1 | 19 | 190 | E2 | H-201 |  |  |  |  | instrument index
PV-2031 | PV-2031 | Pressure control valve | Vacuum off-gas to H-201 - Valve positioner / output | PIC-2031 | CFU-200-PR-PID-015 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO02 | 4 | FAR-100/MC-VDU-A01 | TB02-7/8 | JB-DA-E2-1 | 39/40 | MC-DA-E2-1 | 20 | 190 | E2 | H-201 |  |  |  |  | instrument index
FV-2011 | FV-2011 | Flow control valve | LVGO PA circulation - Valve positioner / output | FIC-2011 | CFU-200-PR-PID-014 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO02 | 5 | FAR-100/MC-VDU-A01 | TB02-9/10 | JB-DA-E3 | 13/14 | MC-DA-E3 | 7 | 270 | E3 | P-201A |  |  |  |  | instrument index
FV-2015 | FV-2015 | Flow control valve | LVGO product - Valve positioner / output | FIC-2015 | CFU-200-PR-PID-014 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO02 | 6 | FAR-100/MC-VDU-A01 | TB02-11/12 | JB-DA-E3 | 15/16 | MC-DA-E3 | 8 | 270 | E3 | P-201A |  |  |  |  | instrument index
FV-2016 | FV-2016 | Flow control valve | HVGO PA circulation - Valve positioner / output | FIC-2016 | CFU-200-PR-PID-014 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO03 | 1 | FAR-100/MC-VDU-A01 | TB03-1/2 | JB-DA-E3 | 17/18 | MC-DA-E3 | 9 | 260 | E3 | P-202A |  |  |  |  | instrument index
FV-2019 | FV-2019 | Flow control valve | HVGO product - Valve positioner / output | FIC-2019 | CFU-200-PR-PID-014 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO03 | 2 | FAR-100/MC-VDU-A01 | TB03-3/4 | JB-DA-E3 | 19/20 | MC-DA-E3 | 10 | 260 | E3 | P-202A |  |  |  |  | instrument index
FV-2022 | FV-2022 | Flow control valve | Slop wax product - Valve positioner / output | FIC-2022 | CFU-200-PR-PID-014 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO03 | 3 | FAR-100/MC-VDU-A01 | TB03-5/6 | JB-DA-E3 | 21/22 | MC-DA-E3 | 11 | 260 | E3 | P-203A |  |  |  |  | instrument index
FV-2025 | FV-2025 | Flow control valve | Vacuum residue product - Valve positioner / output | FIC-2025 | CFU-200-PR-PID-014 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO03 | 4 | FAR-100/MC-VDU-A01 | TB03-7/8 | JB-DA-E3 | 23/24 | MC-DA-E3 | 12 | 250 | E3 | P-204A |  |  |  |  | instrument index
FV-2020 | FV-2020 | Flow control valve | Wash oil to wash bed (critical, min-flow) - Valve positioner / output | FIC-2020 | CFU-200-PR-PID-013 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO03 | 5 | FAR-100/MC-VDU-A01 | TB03-9/10 | JB-DA-E4-1 | 9/10 | MC-DA-E4-1 | 5 | 270 | E4 | C-201 |  |  |  |  | instrument index
FV-2023 | FV-2023 | Flow control valve | C-201 bottom stripping steam - Valve positioner / output | FIC-2023 | CFU-200-PR-PID-013 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO03 | 6 | FAR-100/MC-VDU-A01 | TB03-11/12 | JB-DA-E4-1 | 11/12 | MC-DA-E4-1 | 6 | 270 | E4 | C-201 |  |  |  |  | instrument index
FV-2027 | FV-2027 | Flow control valve | VR quench flow - Valve positioner / output | FIC-2027 | CFU-200-PR-PID-013 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO04 | 1 | FAR-100/MC-VDU-A01 | TB04-1/2 | JB-DA-E4-1 | 13/14 | MC-DA-E4-1 | 7 | 270 | E4 | C-201 |  |  |  |  | instrument index
LV-2028 | LV-2028 | Level control valve | D-201 hotwell water level - Valve positioner / output | LIC-2028 | CFU-200-PR-PID-015 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO04 | 2 | FAR-100/MC-VDU-A01 | TB04-3/4 | JB-DA-E4-1 | 27/28 | MC-DA-E4-1 | 14 | 300 | E4 | D-201 |  |  |  |  | instrument index
LV-2029 | LV-2029 | Level control valve | D-201 slop oil level - Valve positioner / output | LIC-2029 | CFU-200-PR-PID-015 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO04 | 3 | FAR-100/MC-VDU-A01 | TB04-5/6 | JB-DA-E4-1 | 29/30 | MC-DA-E4-1 | 15 | 300 | E4 | D-201 |  |  |  |  | instrument index
PV-2010 | PV-2010 | Pressure control valve | C-201 top pressure (vacuum) - Valve positioner / output | PIC-2010 | CFU-200-PR-PID-013, CFU-200-PR-PID-015 | DCS | VDU | AO | 4-20 mA HART to smart positioner | VDU-AO04 | 4 | FAR-100/MC-VDU-A01 | TB04-7/8 | JB-DA-E4-1 | 35/36 | MC-DA-E4-1 | 18 | 270 | E4 | C-201 |  |  |  |  | instrument index
A-201 XA | A-201 | Motor interface (MCC) | Lvgo cooler A-201 - Motor fault / not available (15 kW) | A-201 |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 1 | FAR-100/MC-VDU-D01 | TB01-1/2 | JB-DD-D3-1 | 13/14 | MC-DD-D3-1 | 7 | 220 | D3 | A-201 |  |  |  |  | equipment.json (MCC hardwired interface)
A-201 XL | A-201 | Motor interface (MCC) | Lvgo cooler A-201 - Motor running (15 kW) | A-201 |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 2 | FAR-100/MC-VDU-D01 | TB01-3/4 | JB-DD-D3-1 | 15/16 | MC-DD-D3-1 | 8 | 220 | D3 | A-201 |  |  |  |  | equipment.json (MCC hardwired interface)
A-202 XA | A-202 | Motor interface (MCC) | Hvgo Product cooler A-202 - Motor fault / not available (37 kW) | A-202 |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 3 | FAR-100/MC-VDU-D01 | TB01-5/6 | JB-DD-E3-1 | 5/6 | MC-DD-E3-1 | 3 | 230 | E3 | A-202 |  |  |  |  | equipment.json (MCC hardwired interface)
A-202 XL | A-202 | Motor interface (MCC) | Hvgo Product cooler A-202 - Motor running (37 kW) | A-202 |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 4 | FAR-100/MC-VDU-D01 | TB01-7/8 | JB-DD-E3-1 | 7/8 | MC-DD-E3-1 | 4 | 230 | E3 | A-202 |  |  |  |  | equipment.json (MCC hardwired interface)
P-201A XA | P-201A | Motor interface (MCC) | LVGO pumparound / product P-201A - Motor fault / not available (110 kW) | P-201A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 5 | FAR-100/MC-VDU-D01 | TB01-9/10 | JB-DD-E3-1 | 13/14 | MC-DD-E3-1 | 7 | 270 | E3 | P-201A |  |  |  |  | equipment.json (MCC hardwired interface)
P-201A XL | P-201A | Motor interface (MCC) | LVGO pumparound / product P-201A - Motor running (110 kW) | P-201A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 6 | FAR-100/MC-VDU-D01 | TB01-11/12 | JB-DD-E3-1 | 15/16 | MC-DD-E3-1 | 8 | 270 | E3 | P-201A |  |  |  |  | equipment.json (MCC hardwired interface)
P-201B XA | P-201B | Motor interface (MCC) | LVGO pumparound / product P-201B - Motor fault / not available (110 kW) | P-201B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 7 | FAR-100/MC-VDU-D01 | TB01-13/14 | JB-DD-E3-1 | 21/22 | MC-DD-E3-1 | 11 | 270 | E3 | P-201B |  |  |  |  | equipment.json (MCC hardwired interface)
P-201B XL | P-201B | Motor interface (MCC) | LVGO pumparound / product P-201B - Motor running (110 kW) | P-201B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 8 | FAR-100/MC-VDU-D01 | TB01-15/16 | JB-DD-E3-1 | 23/24 | MC-DD-E3-1 | 12 | 270 | E3 | P-201B |  |  |  |  | equipment.json (MCC hardwired interface)
P-202A XA | P-202A | Motor interface (MCC) | HVGO pumparound / product P-202A - Motor fault / not available (200 kW) | P-202A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 9 | FAR-100/MC-VDU-D01 | TB01-17/18 | JB-DD-E3-1 | 29/30 | MC-DD-E3-1 | 15 | 260 | E3 | P-202A |  |  |  |  | equipment.json (MCC hardwired interface)
P-202A XL | P-202A | Motor interface (MCC) | HVGO pumparound / product P-202A - Motor running (200 kW) | P-202A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 10 | FAR-100/MC-VDU-D01 | TB01-19/20 | JB-DD-E3-1 | 31/32 | MC-DD-E3-1 | 16 | 260 | E3 | P-202A |  |  |  |  | equipment.json (MCC hardwired interface)
P-202B XA | P-202B | Motor interface (MCC) | HVGO pumparound / product P-202B - Motor fault / not available (200 kW) | P-202B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 11 | FAR-100/MC-VDU-D01 | TB01-21/22 | JB-DD-E3-1 | 37/38 | MC-DD-E3-1 | 19 | 270 | E3 | P-202B |  |  |  |  | equipment.json (MCC hardwired interface)
P-202B XL | P-202B | Motor interface (MCC) | HVGO pumparound / product P-202B - Motor running (200 kW) | P-202B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 12 | FAR-100/MC-VDU-D01 | TB01-23/24 | JB-DD-E3-1 | 39/40 | MC-DD-E3-1 | 20 | 270 | E3 | P-202B |  |  |  |  | equipment.json (MCC hardwired interface)
P-203A XA | P-203A | Motor interface (MCC) | Slop wax P-203A - Motor fault / not available (5.5 kW) | P-203A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 13 | FAR-100/MC-VDU-D01 | TB01-25/26 | JB-DD-E3-1 | 45/46 | MC-DD-E3-1 | 23 | 260 | E3 | P-203A |  |  |  |  | equipment.json (MCC hardwired interface)
P-203A XL | P-203A | Motor interface (MCC) | Slop wax P-203A - Motor running (5.5 kW) | P-203A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 14 | FAR-100/MC-VDU-D01 | TB01-27/28 | JB-DD-E3-1 | 47/48 | MC-DD-E3-1 | 24 | 260 | E3 | P-203A |  |  |  |  | equipment.json (MCC hardwired interface)
P-203B XA | P-203B | Motor interface (MCC) | Slop wax P-203B - Motor fault / not available (5.5 kW) | P-203B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 15 | FAR-100/MC-VDU-D01 | TB01-29/30 | JB-DD-E3-2 | 5/6 | MC-DD-E3-2 | 3 | 260 | E3 | P-203B |  |  |  |  | equipment.json (MCC hardwired interface)
P-203B XL | P-203B | Motor interface (MCC) | Slop wax P-203B - Motor running (5.5 kW) | P-203B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 16 | FAR-100/MC-VDU-D01 | TB01-31/32 | JB-DD-E3-2 | 7/8 | MC-DD-E3-2 | 4 | 260 | E3 | P-203B |  |  |  |  | equipment.json (MCC hardwired interface)
P-204A XA | P-204A | Motor interface (MCC) | Vacuum residue (incl. quench) P-204A - Motor fault / not available (132 kW) | P-204A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 17 | FAR-100/MC-VDU-D01 | TB01-33/34 | JB-DD-E3-2 | 13/14 | MC-DD-E3-2 | 7 | 250 | E3 | P-204A |  |  |  |  | equipment.json (MCC hardwired interface)
P-204A XL | P-204A | Motor interface (MCC) | Vacuum residue (incl. quench) P-204A - Motor running (132 kW) | P-204A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 18 | FAR-100/MC-VDU-D01 | TB01-35/36 | JB-DD-E3-2 | 15/16 | MC-DD-E3-2 | 8 | 250 | E3 | P-204A |  |  |  |  | equipment.json (MCC hardwired interface)
P-204B XA | P-204B | Motor interface (MCC) | Vacuum residue (incl. quench) P-204B - Motor fault / not available (132 kW) | P-204B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 19 | FAR-100/MC-VDU-D01 | TB01-37/38 | JB-DD-E3-2 | 21/22 | MC-DD-E3-2 | 11 | 250 | E3 | P-204B |  |  |  |  | equipment.json (MCC hardwired interface)
P-204B XL | P-204B | Motor interface (MCC) | Vacuum residue (incl. quench) P-204B - Motor running (132 kW) | P-204B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 20 | FAR-100/MC-VDU-D01 | TB01-39/40 | JB-DD-E3-2 | 23/24 | MC-DD-E3-2 | 12 | 250 | E3 | P-204B |  |  |  |  | equipment.json (MCC hardwired interface)
P-205A XA | P-205A | Motor interface (MCC) | Hotwell sour water P-205A - Motor fault / not available (3.7 kW) | P-205A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 21 | FAR-100/MC-VDU-D01 | TB01-41/42 | JB-DD-E4 | 5/6 | MC-DD-E4 | 3 | 310 | E4 | P-205A |  |  |  |  | equipment.json (MCC hardwired interface)
P-205A XL | P-205A | Motor interface (MCC) | Hotwell sour water P-205A - Motor running (3.7 kW) | P-205A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 22 | FAR-100/MC-VDU-D01 | TB01-43/44 | JB-DD-E4 | 7/8 | MC-DD-E4 | 4 | 310 | E4 | P-205A |  |  |  |  | equipment.json (MCC hardwired interface)
P-205B XA | P-205B | Motor interface (MCC) | Hotwell sour water P-205B - Motor fault / not available (3.7 kW) | P-205B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 23 | FAR-100/MC-VDU-D01 | TB01-45/46 | JB-DD-E4 | 13/14 | MC-DD-E4 | 7 | 310 | E4 | P-205B |  |  |  |  | equipment.json (MCC hardwired interface)
P-205B XL | P-205B | Motor interface (MCC) | Hotwell sour water P-205B - Motor running (3.7 kW) | P-205B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 24 | FAR-100/MC-VDU-D01 | TB01-47/48 | JB-DD-E4 | 15/16 | MC-DD-E4 | 8 | 310 | E4 | P-205B |  |  |  |  | equipment.json (MCC hardwired interface)
P-206A XA | P-206A | Motor interface (MCC) | Hotwell slop oil P-206A - Motor fault / not available (0.75 kW) | P-206A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 25 | FAR-100/MC-VDU-D01 | TB01-49/50 | JB-DD-E4 | 21/22 | MC-DD-E4 | 11 | 310 | E4 | P-206A |  |  |  |  | equipment.json (MCC hardwired interface)
P-206A XL | P-206A | Motor interface (MCC) | Hotwell slop oil P-206A - Motor running (0.75 kW) | P-206A |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI01 | 26 | FAR-100/MC-VDU-D01 | TB01-51/52 | JB-DD-E4 | 23/24 | MC-DD-E4 | 12 | 310 | E4 | P-206A |  |  |  |  | equipment.json (MCC hardwired interface)
P-206B XA | P-206B | Motor interface (MCC) | Hotwell slop oil P-206B - Motor fault / not available (0.75 kW) | P-206B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI02 | 1 | FAR-100/MC-VDU-D01 | TB02-1/2 | JB-DD-F4 | 5/6 | MC-DD-F4 | 3 | 320 | F4 | P-206B |  |  |  |  | equipment.json (MCC hardwired interface)
P-206B XL | P-206B | Motor interface (MCC) | Hotwell slop oil P-206B - Motor running (0.75 kW) | P-206B |  | DCS | VDU | DI | 24 VDC dry contact / NAMUR | VDU-DI02 | 2 | FAR-100/MC-VDU-D01 | TB02-3/4 | JB-DD-F4 | 7/8 | MC-DD-F4 | 4 | 320 | F4 | P-206B |  |  |  |  | equipment.json (MCC hardwired interface)
A-201 HS-START | A-201 | Motor interface (MCC) | Lvgo cooler A-201 - Start command (15 kW) | A-201 |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 1 | FAR-100/MC-VDU-D01 | TB01-1/2 | JB-DD-D3-1 | 9/10 | MC-DD-D3-1 | 5 | 220 | D3 | A-201 |  |  |  |  | equipment.json (MCC hardwired interface)
A-201 HS-STOP | A-201 | Motor interface (MCC) | Lvgo cooler A-201 - Stop command (15 kW) | A-201 |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 2 | FAR-100/MC-VDU-D01 | TB01-3/4 | JB-DD-D3-1 | 11/12 | MC-DD-D3-1 | 6 | 220 | D3 | A-201 |  |  |  |  | equipment.json (MCC hardwired interface)
A-202 HS-START | A-202 | Motor interface (MCC) | Hvgo Product cooler A-202 - Start command (37 kW) | A-202 |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 3 | FAR-100/MC-VDU-D01 | TB01-5/6 | JB-DD-E3-1 | 1/2 | MC-DD-E3-1 | 1 | 230 | E3 | A-202 |  |  |  |  | equipment.json (MCC hardwired interface)
A-202 HS-STOP | A-202 | Motor interface (MCC) | Hvgo Product cooler A-202 - Stop command (37 kW) | A-202 |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 4 | FAR-100/MC-VDU-D01 | TB01-7/8 | JB-DD-E3-1 | 3/4 | MC-DD-E3-1 | 2 | 230 | E3 | A-202 |  |  |  |  | equipment.json (MCC hardwired interface)
P-201A HS-START | P-201A | Motor interface (MCC) | LVGO pumparound / product P-201A - Start command (110 kW) | P-201A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 5 | FAR-100/MC-VDU-D01 | TB01-9/10 | JB-DD-E3-1 | 9/10 | MC-DD-E3-1 | 5 | 270 | E3 | P-201A |  |  |  |  | equipment.json (MCC hardwired interface)
P-201A HS-STOP | P-201A | Motor interface (MCC) | LVGO pumparound / product P-201A - Stop command (110 kW) | P-201A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 6 | FAR-100/MC-VDU-D01 | TB01-11/12 | JB-DD-E3-1 | 11/12 | MC-DD-E3-1 | 6 | 270 | E3 | P-201A |  |  |  |  | equipment.json (MCC hardwired interface)
P-201B HS-START | P-201B | Motor interface (MCC) | LVGO pumparound / product P-201B - Start command (110 kW) | P-201B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 7 | FAR-100/MC-VDU-D01 | TB01-13/14 | JB-DD-E3-1 | 17/18 | MC-DD-E3-1 | 9 | 270 | E3 | P-201B |  |  |  |  | equipment.json (MCC hardwired interface)
P-201B HS-STOP | P-201B | Motor interface (MCC) | LVGO pumparound / product P-201B - Stop command (110 kW) | P-201B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 8 | FAR-100/MC-VDU-D01 | TB01-15/16 | JB-DD-E3-1 | 19/20 | MC-DD-E3-1 | 10 | 270 | E3 | P-201B |  |  |  |  | equipment.json (MCC hardwired interface)
P-202A HS-START | P-202A | Motor interface (MCC) | HVGO pumparound / product P-202A - Start command (200 kW) | P-202A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 9 | FAR-100/MC-VDU-D01 | TB01-17/18 | JB-DD-E3-1 | 25/26 | MC-DD-E3-1 | 13 | 260 | E3 | P-202A |  |  |  |  | equipment.json (MCC hardwired interface)
P-202A HS-STOP | P-202A | Motor interface (MCC) | HVGO pumparound / product P-202A - Stop command (200 kW) | P-202A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 10 | FAR-100/MC-VDU-D01 | TB01-19/20 | JB-DD-E3-1 | 27/28 | MC-DD-E3-1 | 14 | 260 | E3 | P-202A |  |  |  |  | equipment.json (MCC hardwired interface)
P-202B HS-START | P-202B | Motor interface (MCC) | HVGO pumparound / product P-202B - Start command (200 kW) | P-202B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 11 | FAR-100/MC-VDU-D01 | TB01-21/22 | JB-DD-E3-1 | 33/34 | MC-DD-E3-1 | 17 | 270 | E3 | P-202B |  |  |  |  | equipment.json (MCC hardwired interface)
P-202B HS-STOP | P-202B | Motor interface (MCC) | HVGO pumparound / product P-202B - Stop command (200 kW) | P-202B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 12 | FAR-100/MC-VDU-D01 | TB01-23/24 | JB-DD-E3-1 | 35/36 | MC-DD-E3-1 | 18 | 270 | E3 | P-202B |  |  |  |  | equipment.json (MCC hardwired interface)
P-203A HS-START | P-203A | Motor interface (MCC) | Slop wax P-203A - Start command (5.5 kW) | P-203A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO01 | 13 | FAR-100/MC-VDU-D01 | TB01-25/26 | JB-DD-E3-1 | 41/42 | MC-DD-E3-1 | 21 | 260 | E3 | P-203A |  |  |  |  | equipment.json (MCC hardwired interface)
P-203A HS-STOP | P-203A | Motor interface (MCC) | Slop wax P-203A - Stop command (5.5 kW) | P-203A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 1 | FAR-100/MC-VDU-D01 | TB02-1/2 | JB-DD-E3-1 | 43/44 | MC-DD-E3-1 | 22 | 260 | E3 | P-203A |  |  |  |  | equipment.json (MCC hardwired interface)
P-203B HS-START | P-203B | Motor interface (MCC) | Slop wax P-203B - Start command (5.5 kW) | P-203B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 2 | FAR-100/MC-VDU-D01 | TB02-3/4 | JB-DD-E3-2 | 1/2 | MC-DD-E3-2 | 1 | 260 | E3 | P-203B |  |  |  |  | equipment.json (MCC hardwired interface)
P-203B HS-STOP | P-203B | Motor interface (MCC) | Slop wax P-203B - Stop command (5.5 kW) | P-203B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 3 | FAR-100/MC-VDU-D01 | TB02-5/6 | JB-DD-E3-2 | 3/4 | MC-DD-E3-2 | 2 | 260 | E3 | P-203B |  |  |  |  | equipment.json (MCC hardwired interface)
P-204A HS-START | P-204A | Motor interface (MCC) | Vacuum residue (incl. quench) P-204A - Start command (132 kW) | P-204A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 4 | FAR-100/MC-VDU-D01 | TB02-7/8 | JB-DD-E3-2 | 9/10 | MC-DD-E3-2 | 5 | 250 | E3 | P-204A |  |  |  |  | equipment.json (MCC hardwired interface)
P-204A HS-STOP | P-204A | Motor interface (MCC) | Vacuum residue (incl. quench) P-204A - Stop command (132 kW) | P-204A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 5 | FAR-100/MC-VDU-D01 | TB02-9/10 | JB-DD-E3-2 | 11/12 | MC-DD-E3-2 | 6 | 250 | E3 | P-204A |  |  |  |  | equipment.json (MCC hardwired interface)
P-204B HS-START | P-204B | Motor interface (MCC) | Vacuum residue (incl. quench) P-204B - Start command (132 kW) | P-204B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 6 | FAR-100/MC-VDU-D01 | TB02-11/12 | JB-DD-E3-2 | 17/18 | MC-DD-E3-2 | 9 | 250 | E3 | P-204B |  |  |  |  | equipment.json (MCC hardwired interface)
P-204B HS-STOP | P-204B | Motor interface (MCC) | Vacuum residue (incl. quench) P-204B - Stop command (132 kW) | P-204B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 7 | FAR-100/MC-VDU-D01 | TB02-13/14 | JB-DD-E3-2 | 19/20 | MC-DD-E3-2 | 10 | 250 | E3 | P-204B |  |  |  |  | equipment.json (MCC hardwired interface)
P-205A HS-START | P-205A | Motor interface (MCC) | Hotwell sour water P-205A - Start command (3.7 kW) | P-205A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 8 | FAR-100/MC-VDU-D01 | TB02-15/16 | JB-DD-E4 | 1/2 | MC-DD-E4 | 1 | 310 | E4 | P-205A |  |  |  |  | equipment.json (MCC hardwired interface)
P-205A HS-STOP | P-205A | Motor interface (MCC) | Hotwell sour water P-205A - Stop command (3.7 kW) | P-205A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 9 | FAR-100/MC-VDU-D01 | TB02-17/18 | JB-DD-E4 | 3/4 | MC-DD-E4 | 2 | 310 | E4 | P-205A |  |  |  |  | equipment.json (MCC hardwired interface)
P-205B HS-START | P-205B | Motor interface (MCC) | Hotwell sour water P-205B - Start command (3.7 kW) | P-205B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 10 | FAR-100/MC-VDU-D01 | TB02-19/20 | JB-DD-E4 | 9/10 | MC-DD-E4 | 5 | 310 | E4 | P-205B |  |  |  |  | equipment.json (MCC hardwired interface)
P-205B HS-STOP | P-205B | Motor interface (MCC) | Hotwell sour water P-205B - Stop command (3.7 kW) | P-205B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 11 | FAR-100/MC-VDU-D01 | TB02-21/22 | JB-DD-E4 | 11/12 | MC-DD-E4 | 6 | 310 | E4 | P-205B |  |  |  |  | equipment.json (MCC hardwired interface)
P-206A HS-START | P-206A | Motor interface (MCC) | Hotwell slop oil P-206A - Start command (0.75 kW) | P-206A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 12 | FAR-100/MC-VDU-D01 | TB02-23/24 | JB-DD-E4 | 17/18 | MC-DD-E4 | 9 | 310 | E4 | P-206A |  |  |  |  | equipment.json (MCC hardwired interface)
P-206A HS-STOP | P-206A | Motor interface (MCC) | Hotwell slop oil P-206A - Stop command (0.75 kW) | P-206A |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO02 | 13 | FAR-100/MC-VDU-D01 | TB02-25/26 | JB-DD-E4 | 19/20 | MC-DD-E4 | 10 | 310 | E4 | P-206A |  |  |  |  | equipment.json (MCC hardwired interface)
P-206B HS-START | P-206B | Motor interface (MCC) | Hotwell slop oil P-206B - Start command (0.75 kW) | P-206B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO03 | 1 | FAR-100/MC-VDU-D01 | TB03-1/2 | JB-DD-F4 | 1/2 | MC-DD-F4 | 1 | 320 | F4 | P-206B |  |  |  |  | equipment.json (MCC hardwired interface)
P-206B HS-STOP | P-206B | Motor interface (MCC) | Hotwell slop oil P-206B - Stop command (0.75 kW) | P-206B |  | DCS | VDU | DO | 24 VDC interposing relay | VDU-DO03 | 2 | FAR-100/MC-VDU-D01 | TB03-3/4 | JB-DD-F4 | 3/4 | MC-DD-F4 | 2 | 320 | F4 | P-206B |  |  |  |  | equipment.json (MCC hardwired interface)
LT-1007B | LT-1007B | Level transmitter | D-101A/B low-low interface (grid short) -> trip transformers | LIC-1007 | CFU-100-PR-PID-002 | SIS | SIS-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | SIS-1-AI01 | 1 | FAR-100/SMC-SIS-1-A01 | TB01-1/2 | JB-SA-A2 | 1/2 | MC-SA-A2 | 1 | 90 | A2 | D-101A | SIF-107 | SIL 1 | 0-100 | % | instrument index
LT-1008B | LT-1008B | Level transmitter | D-101A/B low-low interface (grid short) -> trip transformers | LIC-1008 | CFU-100-PR-PID-002 | SIS | SIS-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | SIS-1-AI01 | 2 | FAR-100/SMC-SIS-1-A01 | TB01-3/4 | JB-SA-A2 | 3/4 | MC-SA-A2 | 2 | 90 | A2 | D-101A | SIF-107 | SIL 1 | 0-100 | % | instrument index
LT-1092B | LT-1092B | Level transmitter | D-105 low-low level -> close LPG product XV (gas blow-by to LPG treating) | LIC-1092 | CFU-100-PR-PID-010 | SIS | SIS-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | SIS-1-AI01 | 3 | FAR-100/SMC-SIS-1-A01 | TB01-5/6 | JB-SA-B4 | 1/2 | MC-SA-B4 | 1 | 130 | B4 | D-105 | SIF-109 | SIL 1 | 0-100 | % | instrument index
PT-1091B | PT-1091B | Pressure transmitter | C-105 high-high pressure -> cut reboiler steam | PIC-1091 | CFU-100-PR-PID-010 | SIS | SIS-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | SIS-1-AI01 | 4 | FAR-100/SMC-SIS-1-A01 | TB01-7/8 | JB-SA-B4 | 3/4 | MC-SA-B4 | 2 | 140 | B4 | C-105 | SIF-110 | SIL 1 | 0-20 | barg | instrument index
LT-1082B | LT-1082B | Level transmitter | C-101 high-high bottom level -> stop P-101 / close FV-1001 | LIC-1082 | CFU-100-PR-PID-006 | SIS | SIS-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | SIS-1-AI01 | 5 | FAR-100/SMC-SIS-1-A01 | TB01-9/10 | JB-SA-C4 | 1/2 | MC-SA-C4 | 1 | 170 | C4 | C-101 | SIF-108 | SIL 1 | 0-100 | % | instrument index
LT-2024B | LT-2024B | Level transmitter | C-201 high-high bottom level -> trip FV-1083 / P-112 | LIC-2024 | CFU-200-PR-PID-013 | SIS | SIS-1 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | SIS-1-AI01 | 6 | FAR-100/SMC-SIS-1-A01 | TB01-11/12 | JB-SA-E4 | 1/2 | MC-SA-E4 | 1 | 270 | E4 | C-201 | SIF-203 | SIL 1 | 0-100 | % | instrument index
ZSC-1093 | XV-1093 | On/off shutdown valve | D-105 low-low level -> close LPG product XV (gas blow-by to LPG treating) - Closed limit switch | FIC-1093 | CFU-100-PR-PID-010 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 1 | FAR-100/SMC-SIS-1-D01 | TB01-1/2 | JB-SD-B4 | 5/6 | MC-SD-B4 | 3 | 130 | B4 | D-105 | SIF-109 | SIL 1 |  |  | instrument index
ZSC-1096 | XV-1096 | On/off shutdown valve | C-105 high-high pressure -> cut reboiler steam - Closed limit switch | FIC-1096 | CFU-100-PR-PID-010 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 2 | FAR-100/SMC-SIS-1-D01 | TB01-3/4 | JB-SD-B4 | 7/8 | MC-SD-B4 | 4 | 140 | B4 | C-105 | SIF-110 | SIL 1 |  |  | instrument index
ZSO-1093 | XV-1093 | On/off shutdown valve | D-105 low-low level -> close LPG product XV (gas blow-by to LPG treating) - Open limit switch | FIC-1093 | CFU-100-PR-PID-010 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 3 | FAR-100/SMC-SIS-1-D01 | TB01-5/6 | JB-SD-B4 | 9/10 | MC-SD-B4 | 5 | 130 | B4 | D-105 | SIF-109 | SIL 1 |  |  | instrument index
ZSO-1096 | XV-1096 | On/off shutdown valve | C-105 high-high pressure -> cut reboiler steam - Open limit switch | FIC-1096 | CFU-100-PR-PID-010 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 4 | FAR-100/SMC-SIS-1-D01 | TB01-7/8 | JB-SD-B4 | 11/12 | MC-SD-B4 | 6 | 140 | B4 | C-105 | SIF-110 | SIL 1 |  |  | instrument index
ZSC-1121 | EIV-1121 | Emergency isolation valve (ROSOV) | Pump P-112/P-204 hot-pump emergency isolation (fire) - Closed limit switch | EIV-1121 | CFU-100-PR-PID-006 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 5 | FAR-100/SMC-SIS-1-D01 | TB01-9/10 | JB-SD-C3 | 9/10 | MC-SD-C3 | 5 | 150 | C3 | P-112A | SIF-204 | SIL 1 |  |  | instrument index
ZSC-2041 | EIV-2041 | Emergency isolation valve (ROSOV) | Pump P-112/P-204 hot-pump emergency isolation (fire) - Closed limit switch | EIV-2041 | CFU-200-PR-PID-013 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 6 | FAR-100/SMC-SIS-1-D01 | TB01-11/12 | JB-SD-C3 | 11/12 | MC-SD-C3 | 6 | 150 | C3 | P-112A | SIF-204 | SIL 1 |  |  | instrument index
ZSO-1121 | EIV-1121 | Emergency isolation valve (ROSOV) | Pump P-112/P-204 hot-pump emergency isolation (fire) - Open limit switch | EIV-1121 | CFU-100-PR-PID-006 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 7 | FAR-100/SMC-SIS-1-D01 | TB01-13/14 | JB-SD-C3 | 13/14 | MC-SD-C3 | 7 | 150 | C3 | P-112A | SIF-204 | SIL 1 |  |  | instrument index
ZSO-2041 | EIV-2041 | Emergency isolation valve (ROSOV) | Pump P-112/P-204 hot-pump emergency isolation (fire) - Open limit switch | EIV-2041 | CFU-200-PR-PID-013 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 8 | FAR-100/SMC-SIS-1-D01 | TB01-15/16 | JB-SD-C3 | 15/16 | MC-SD-C3 | 8 | 150 | C3 | P-112A | SIF-204 | SIL 1 |  |  | instrument index
HS-1121 | HS-1121 | Hand switch | EIV-1121 manual close (CCR + field) | HS-1121 | CFU-100-PR-PID-006 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 9 | FAR-100/SMC-SIS-1-D01 | TB01-17/18 | JB-SD-C4 | 1/2 | MC-SD-C4 | 1 | 170 | C4 | C-101 | SIF-204 | SIL 1 |  |  | instrument index
ZSC-1001 | XV-1001 | On/off shutdown valve | C-101 high-high bottom level -> stop P-101 / close FV-1001 - Closed limit switch | FIC-1001 | CFU-100-PR-PID-001 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 10 | FAR-100/SMC-SIS-1-D01 | TB01-19/20 | JB-SD-C4 | 5/6 | MC-SD-C4 | 3 | 170 | C4 | C-101 | SIF-108 | SIL 1 |  |  | instrument index
ZSO-1001 | XV-1001 | On/off shutdown valve | C-101 high-high bottom level -> stop P-101 / close FV-1001 - Open limit switch | FIC-1001 | CFU-100-PR-PID-001 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 11 | FAR-100/SMC-SIS-1-D01 | TB01-21/22 | JB-SD-C4 | 7/8 | MC-SD-C4 | 4 | 170 | C4 | C-101 | SIF-108 | SIL 1 |  |  | instrument index
HS-9000 | HS-9000 | Hand switch | Unit ESD push-button (CCR + field) | HS-9000 | CFU-900-PR-PID-016 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 12 | FAR-100/SMC-SIS-1-D01 | TB01-23/24 | JB-SD-D1 | 1/2 | MC-SD-D1 | 1 | 140 | D1 | D-103 | SIF-901 | SIL 2 |  |  | instrument index
HS-2041 | HS-2041 | Hand switch | EIV-2041 manual close (CCR + field) | HS-2041 | CFU-200-PR-PID-013 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 13 | FAR-100/SMC-SIS-1-D01 | TB01-25/26 | JB-SD-E4 | 1/2 | MC-SD-E4 | 1 | 270 | E4 | C-201 | SIF-204 | SIL 1 |  |  | instrument index
ZSC-1083 | XV-1083 | On/off shutdown valve | C-201 high-high bottom level -> trip FV-1083 / P-112 - Closed limit switch | FIC-1083 | CFU-100-PR-PID-006 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 14 | FAR-100/SMC-SIS-1-D01 | TB01-27/28 | JB-SD-E4 | 5/6 | MC-SD-E4 | 3 | 270 | E4 | C-201 | SIF-203 | SIL 1 |  |  | instrument index
ZSO-1083 | XV-1083 | On/off shutdown valve | C-201 high-high bottom level -> trip FV-1083 / P-112 - Open limit switch | FIC-1083 | CFU-100-PR-PID-006 | SIS | SIS-1 | DI | 24 VDC dry contact / NAMUR | SIS-1-DI01 | 15 | FAR-100/SMC-SIS-1-D01 | TB01-29/30 | JB-SD-E4 | 7/8 | MC-SD-E4 | 4 | 270 | E4 | C-201 | SIF-203 | SIL 1 |  |  | instrument index
XY-1007 | XY-1007 | Trip relay output | D-101A transformer feeder trip | LIC-1007 | CFU-100-PR-PID-002 | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 1 | FAR-100/SMC-SIS-1-D01 | TB01-1/2 | JB-SD-A2 | 1/2 | MC-SD-A2 | 1 | 90 | A2 | D-101A | SIF-107 | SIL 1 |  |  | instrument index
XY-1008 | XY-1008 | Trip relay output | D-101B transformer feeder trip | LIC-1008 | CFU-100-PR-PID-002 | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 2 | FAR-100/SMC-SIS-1-D01 | TB01-3/4 | JB-SD-A2 | 3/4 | MC-SD-A2 | 2 | 80 | A2 | D-101B | SIF-107 | SIL 1 |  |  | instrument index
XY-P-101A | P-101A | Motor trip relay (SIS) | P-101A trip (C-101 LZHH / ESD) | SIF-108 |  | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 3 | FAR-100/SMC-SIS-1-D01 | TB01-5/6 | JB-SD-A3 | 1/2 | MC-SD-A3 | 1 | 160 | A3 | P-101A | SIF-108 | SIL 1 |  |  | C&E CFU-000-IC-CE-001
XY-P-101B | P-101B | Motor trip relay (SIS) | P-101B trip (C-101 LZHH / ESD) | SIF-108 |  | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 4 | FAR-100/SMC-SIS-1-D01 | TB01-7/8 | JB-SD-A3 | 3/4 | MC-SD-A3 | 2 | 150 | A3 | P-101B | SIF-108 | SIL 1 |  |  | C&E CFU-000-IC-CE-001
XY-P-102A | P-102A | Motor trip relay (SIS) | P-102A trip (ESD) | SIF-901 |  | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 5 | FAR-100/SMC-SIS-1-D01 | TB01-9/10 | JB-SD-B3 | 1/2 | MC-SD-B3 | 1 | 100 | B3 | P-102A | SIF-901 | SIL 2 |  |  | C&E CFU-000-IC-CE-001
XY-P-102B | P-102B | Motor trip relay (SIS) | P-102B trip (ESD) | SIF-901 |  | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 6 | FAR-100/SMC-SIS-1-D01 | TB01-11/12 | JB-SD-B3 | 3/4 | MC-SD-B3 | 2 | 90 | B3 | P-102B | SIF-901 | SIL 2 |  |  | C&E CFU-000-IC-CE-001
XV-1093 | XV-1093 | On/off shutdown valve | D-105 low-low level -> close LPG product XV (gas blow-by to LPG treating) - SOV de-energise to trip | FIC-1093 | CFU-100-PR-PID-010 | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 7 | FAR-100/SMC-SIS-1-D01 | TB01-13/14 | JB-SD-B4 | 1/2 | MC-SD-B4 | 1 | 130 | B4 | D-105 | SIF-109 | SIL 1 |  |  | instrument index
XV-1096 | XV-1096 | On/off shutdown valve | C-105 high-high pressure -> cut reboiler steam - SOV de-energise to trip | FIC-1096 | CFU-100-PR-PID-010 | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 8 | FAR-100/SMC-SIS-1-D01 | TB01-15/16 | JB-SD-B4 | 3/4 | MC-SD-B4 | 2 | 140 | B4 | C-105 | SIF-110 | SIL 1 |  |  | instrument index
EIV-1121 | EIV-1121 | Emergency isolation valve (ROSOV) | Pump P-112/P-204 hot-pump emergency isolation (fire) - SOV de-energise to trip | EIV-1121 | CFU-100-PR-PID-006 | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 9 | FAR-100/SMC-SIS-1-D01 | TB01-17/18 | JB-SD-C3 | 1/2 | MC-SD-C3 | 1 | 150 | C3 | P-112A | SIF-204 | SIL 1 |  |  | instrument index
EIV-2041 | EIV-2041 | Emergency isolation valve (ROSOV) | Pump P-112/P-204 hot-pump emergency isolation (fire) - SOV de-energise to trip | EIV-2041 | CFU-200-PR-PID-013 | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 10 | FAR-100/SMC-SIS-1-D01 | TB01-19/20 | JB-SD-C3 | 3/4 | MC-SD-C3 | 2 | 150 | C3 | P-112A | SIF-204 | SIL 1 |  |  | instrument index
XY-P-112A | P-112A | Motor trip relay (SIS) | P-112A trip (C-201 LZHH / fire / ESD) | SIF-203 |  | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 11 | FAR-100/SMC-SIS-1-D01 | TB01-21/22 | JB-SD-C3 | 5/6 | MC-SD-C3 | 3 | 150 | C3 | P-112A | SIF-203 | SIL 1 |  |  | C&E CFU-000-IC-CE-001
XY-P-112B | P-112B | Motor trip relay (SIS) | P-112B trip (C-201 LZHH / fire / ESD) | SIF-203 |  | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 12 | FAR-100/SMC-SIS-1-D01 | TB01-23/24 | JB-SD-C3 | 7/8 | MC-SD-C3 | 4 | 160 | C3 | P-112B | SIF-203 | SIL 1 |  |  | C&E CFU-000-IC-CE-001
XV-1001 | XV-1001 | On/off shutdown valve | C-101 high-high bottom level -> stop P-101 / close FV-1001 - SOV de-energise to trip | FIC-1001 | CFU-100-PR-PID-001 | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO01 | 13 | FAR-100/SMC-SIS-1-D01 | TB01-25/26 | JB-SD-C4 | 3/4 | MC-SD-C4 | 2 | 170 | C4 | C-101 | SIF-108 | SIL 1 |  |  | instrument index
XY-P-204A | P-204A | Motor trip relay (SIS) | P-204A trip (fire) | SIF-204 |  | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO02 | 1 | FAR-100/SMC-SIS-1-D01 | TB02-1/2 | JB-SD-E3 | 1/2 | MC-SD-E3 | 1 | 250 | E3 | P-204A | SIF-204 | SIL 1 |  |  | C&E CFU-000-IC-CE-001
XY-P-204B | P-204B | Motor trip relay (SIS) | P-204B trip (fire) | SIF-204 |  | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO02 | 2 | FAR-100/SMC-SIS-1-D01 | TB02-3/4 | JB-SD-E3 | 3/4 | MC-SD-E3 | 2 | 250 | E3 | P-204B | SIF-204 | SIL 1 |  |  | C&E CFU-000-IC-CE-001
XV-1083 | XV-1083 | On/off shutdown valve | C-201 high-high bottom level -> trip FV-1083 / P-112 - SOV de-energise to trip | FIC-1083 | CFU-100-PR-PID-006 | SIS | SIS-1 | DO | 24 VDC, de-energise to trip | SIS-1-DO02 | 3 | FAR-100/SMC-SIS-1-D01 | TB02-5/6 | JB-SD-E4 | 3/4 | MC-SD-E4 | 2 | 270 | E4 | C-201 | SIF-203 | SIL 1 |  |  | instrument index
FT-1011A | FT-1011A | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1011 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 1 | FAR-100/SMC-BMS-H101-A01 | TB01-1/2 | JB-BA-C2-1 | 1/2 | MC-BA-C2-1 | 1 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1011B | FT-1011B | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1011 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 2 | FAR-100/SMC-BMS-H101-A01 | TB01-3/4 | JB-BA-C2-1 | 3/4 | MC-BA-C2-1 | 2 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1011C | FT-1011C | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1011 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 3 | FAR-100/SMC-BMS-H101-A01 | TB01-5/6 | JB-BA-C2-1 | 5/6 | MC-BA-C2-1 | 3 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1012A | FT-1012A | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1012 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 4 | FAR-100/SMC-BMS-H101-A01 | TB01-7/8 | JB-BA-C2-1 | 7/8 | MC-BA-C2-1 | 4 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1012B | FT-1012B | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1012 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 5 | FAR-100/SMC-BMS-H101-A01 | TB01-9/10 | JB-BA-C2-1 | 9/10 | MC-BA-C2-1 | 5 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1012C | FT-1012C | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1012 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 6 | FAR-100/SMC-BMS-H101-A01 | TB01-11/12 | JB-BA-C2-1 | 11/12 | MC-BA-C2-1 | 6 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1013A | FT-1013A | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1013 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 7 | FAR-100/SMC-BMS-H101-A01 | TB01-13/14 | JB-BA-C2-1 | 13/14 | MC-BA-C2-1 | 7 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1013B | FT-1013B | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1013 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 8 | FAR-100/SMC-BMS-H101-A01 | TB01-15/16 | JB-BA-C2-1 | 15/16 | MC-BA-C2-1 | 8 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1013C | FT-1013C | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1013 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 9 | FAR-100/SMC-BMS-H101-A01 | TB01-17/18 | JB-BA-C2-1 | 17/18 | MC-BA-C2-1 | 9 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1014A | FT-1014A | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1014 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 10 | FAR-100/SMC-BMS-H101-A01 | TB01-19/20 | JB-BA-C2-1 | 19/20 | MC-BA-C2-1 | 10 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1014B | FT-1014B | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1014 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 11 | FAR-100/SMC-BMS-H101-A01 | TB01-21/22 | JB-BA-C2-1 | 21/22 | MC-BA-C2-1 | 11 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1014C | FT-1014C | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1014 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 12 | FAR-100/SMC-BMS-H101-A01 | TB01-23/24 | JB-BA-C2-1 | 23/24 | MC-BA-C2-1 | 12 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1015A | FT-1015A | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1015 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI01 | 13 | FAR-100/SMC-BMS-H101-A01 | TB01-25/26 | JB-BA-C2-1 | 25/26 | MC-BA-C2-1 | 13 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1015B | FT-1015B | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1015 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 1 | FAR-100/SMC-BMS-H101-A01 | TB02-1/2 | JB-BA-C2-1 | 27/28 | MC-BA-C2-1 | 14 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1015C | FT-1015C | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1015 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 2 | FAR-100/SMC-BMS-H101-A01 | TB02-3/4 | JB-BA-C2-1 | 29/30 | MC-BA-C2-1 | 15 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1016A | FT-1016A | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1016 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 3 | FAR-100/SMC-BMS-H101-A01 | TB02-5/6 | JB-BA-C2-1 | 31/32 | MC-BA-C2-1 | 16 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1016B | FT-1016B | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1016 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 4 | FAR-100/SMC-BMS-H101-A01 | TB02-7/8 | JB-BA-C2-1 | 33/34 | MC-BA-C2-1 | 17 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1016C | FT-1016C | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1016 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 5 | FAR-100/SMC-BMS-H101-A01 | TB02-9/10 | JB-BA-C2-1 | 35/36 | MC-BA-C2-1 | 18 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1017A | FT-1017A | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1017 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 6 | FAR-100/SMC-BMS-H101-A01 | TB02-11/12 | JB-BA-C2-1 | 37/38 | MC-BA-C2-1 | 19 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1017B | FT-1017B | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1017 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 7 | FAR-100/SMC-BMS-H101-A01 | TB02-13/14 | JB-BA-C2-1 | 39/40 | MC-BA-C2-1 | 20 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1017C | FT-1017C | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1017 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 8 | FAR-100/SMC-BMS-H101-A01 | TB02-15/16 | JB-BA-C2-1 | 41/42 | MC-BA-C2-1 | 21 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1018A | FT-1018A | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1018 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 9 | FAR-100/SMC-BMS-H101-A01 | TB02-17/18 | JB-BA-C2-1 | 43/44 | MC-BA-C2-1 | 22 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1018B | FT-1018B | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1018 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 10 | FAR-100/SMC-BMS-H101-A01 | TB02-19/20 | JB-BA-C2-1 | 45/46 | MC-BA-C2-1 | 23 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
FT-1018C | FT-1018C | Flow transmitter | H-101 low-low pass flow (any pass) -> trip fuel | FIC-1018 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 11 | FAR-100/SMC-BMS-H101-A01 | TB02-21/22 | JB-BA-C2-1 | 47/48 | MC-BA-C2-1 | 24 | 100 | C2 | H-101 | SIF-101 | SIL 2 | 0-100000 | kg/h | instrument index
PT-1027A | PT-1027A | Pressure transmitter | H-101 low-low fuel gas pressure -> trip fuel | PT-1027A | CFU-100-PR-PID-005 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 12 | FAR-100/SMC-BMS-H101-A01 | TB02-23/24 | JB-BA-C2-2 | 1/2 | MC-BA-C2-2 | 1 | 100 | C2 | H-101 | SIF-102 | SIL 1 | 0-5 | barg | instrument index
PT-1027B | PT-1027B | Pressure transmitter | H-101 low-low fuel gas pressure -> trip fuel | PT-1027B | CFU-100-PR-PID-005 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI02 | 13 | FAR-100/SMC-BMS-H101-A01 | TB02-25/26 | JB-BA-C2-2 | 3/4 | MC-BA-C2-2 | 2 | 100 | C2 | H-101 | SIF-102 | SIL 1 | 0-5 | barg | instrument index
PT-1027C | PT-1027C | Pressure transmitter | H-101 low-low fuel gas pressure -> trip fuel | PT-1027C | CFU-100-PR-PID-005 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI03 | 1 | FAR-100/SMC-BMS-H101-A01 | TB03-1/2 | JB-BA-C2-2 | 5/6 | MC-BA-C2-2 | 3 | 100 | C2 | H-101 | SIF-102 | SIL 1 | 0-5 | barg | instrument index
PT-1029A | PT-1029A | Pressure transmitter | H-101 high-high arch pressure / loss of ID fan -> trip | PT-1029A | CFU-100-PR-PID-005 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI03 | 2 | FAR-100/SMC-BMS-H101-A01 | TB03-3/4 | JB-BA-C2-2 | 7/8 | MC-BA-C2-2 | 4 | 100 | C2 | H-101 | SIF-105 | SIL 1 | -25-25 | mmH2O | instrument index
PT-1029B | PT-1029B | Pressure transmitter | H-101 high-high arch pressure / loss of ID fan -> trip | PT-1029B | CFU-100-PR-PID-005 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI03 | 3 | FAR-100/SMC-BMS-H101-A01 | TB03-5/6 | JB-BA-C2-2 | 9/10 | MC-BA-C2-2 | 5 | 100 | C2 | H-101 | SIF-105 | SIL 1 | -25-25 | mmH2O | instrument index
PT-1029C | PT-1029C | Pressure transmitter | H-101 high-high arch pressure / loss of ID fan -> trip | PT-1029C | CFU-100-PR-PID-005 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI03 | 4 | FAR-100/SMC-BMS-H101-A01 | TB03-7/8 | JB-BA-C2-2 | 11/12 | MC-BA-C2-2 | 6 | 100 | C2 | H-101 | SIF-105 | SIL 1 | -25-25 | mmH2O | instrument index
TT-1020A | TT-1020A | Temperature transmitter | H-101 high-high COT -> trip fuel | TIC-1020 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI03 | 5 | FAR-100/SMC-BMS-H101-A01 | TB03-9/10 | JB-BA-C2-2 | 13/14 | MC-BA-C2-2 | 7 | 100 | C2 | H-101 | SIF-106 | SIL 1 | 0-500 | C | instrument index
TT-1020B | TT-1020B | Temperature transmitter | H-101 high-high COT -> trip fuel | TIC-1020 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI03 | 6 | FAR-100/SMC-BMS-H101-A01 | TB03-11/12 | JB-BA-C2-2 | 15/16 | MC-BA-C2-2 | 8 | 100 | C2 | H-101 | SIF-106 | SIL 1 | 0-500 | C | instrument index
TT-1020C | TT-1020C | Temperature transmitter | H-101 high-high COT -> trip fuel | TIC-1020 | CFU-100-PR-PID-004 | BMS | BMS-H101 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H101-AI03 | 7 | FAR-100/SMC-BMS-H101-A01 | TB03-13/14 | JB-BA-C2-2 | 17/18 | MC-BA-C2-2 | 9 | 100 | C2 | H-101 | SIF-106 | SIL 1 | 0-500 | C | instrument index
BS-1028-01 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 1 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 1 | FAR-100/SMC-BMS-H101-D01 | TB01-1/2 | JB-BD-C2-1 | 1/2 | MC-BD-C2-1 | 1 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-02 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 2 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 2 | FAR-100/SMC-BMS-H101-D01 | TB01-3/4 | JB-BD-C2-1 | 3/4 | MC-BD-C2-1 | 2 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-03 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 3 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 3 | FAR-100/SMC-BMS-H101-D01 | TB01-5/6 | JB-BD-C2-1 | 5/6 | MC-BD-C2-1 | 3 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-04 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 4 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 4 | FAR-100/SMC-BMS-H101-D01 | TB01-7/8 | JB-BD-C2-1 | 7/8 | MC-BD-C2-1 | 4 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-05 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 5 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 5 | FAR-100/SMC-BMS-H101-D01 | TB01-9/10 | JB-BD-C2-1 | 9/10 | MC-BD-C2-1 | 5 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-06 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 6 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 6 | FAR-100/SMC-BMS-H101-D01 | TB01-11/12 | JB-BD-C2-1 | 11/12 | MC-BD-C2-1 | 6 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-07 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 7 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 7 | FAR-100/SMC-BMS-H101-D01 | TB01-13/14 | JB-BD-C2-1 | 13/14 | MC-BD-C2-1 | 7 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-08 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 8 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 8 | FAR-100/SMC-BMS-H101-D01 | TB01-15/16 | JB-BD-C2-1 | 15/16 | MC-BD-C2-1 | 8 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-09 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 9 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 9 | FAR-100/SMC-BMS-H101-D01 | TB01-17/18 | JB-BD-C2-1 | 17/18 | MC-BD-C2-1 | 9 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-10 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 10 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 10 | FAR-100/SMC-BMS-H101-D01 | TB01-19/20 | JB-BD-C2-1 | 19/20 | MC-BD-C2-1 | 10 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-11 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 11 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 11 | FAR-100/SMC-BMS-H101-D01 | TB01-21/22 | JB-BD-C2-1 | 21/22 | MC-BD-C2-1 | 11 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-12 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 12 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 12 | FAR-100/SMC-BMS-H101-D01 | TB01-23/24 | JB-BD-C2-1 | 23/24 | MC-BD-C2-1 | 12 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-13 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 13 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 13 | FAR-100/SMC-BMS-H101-D01 | TB01-25/26 | JB-BD-C2-1 | 25/26 | MC-BD-C2-1 | 13 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-14 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 14 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 14 | FAR-100/SMC-BMS-H101-D01 | TB01-27/28 | JB-BD-C2-1 | 27/28 | MC-BD-C2-1 | 14 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-15 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 15 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 15 | FAR-100/SMC-BMS-H101-D01 | TB01-29/30 | JB-BD-C2-1 | 29/30 | MC-BD-C2-1 | 15 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
BS-1028-16 | BS-1028 | Flame scanner | H-101 flame scanners (1 per burner, 16 off) - Flame scanner burner 16 (flame on) | BS-1028 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 16 | FAR-100/SMC-BMS-H101-D01 | TB01-31/32 | JB-BD-C2-1 | 31/32 | MC-BD-C2-1 | 16 | 100 | C2 | H-101 |  |  | Flame ON/OFF | - | instrument index
ZSC-1021 | XV-1021 | On/off shutdown valve | H-101 main fuel gas SSOV - Closed limit switch | PIC-1021 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 17 | FAR-100/SMC-BMS-H101-D01 | TB01-33/34 | JB-BD-C2-1 | 41/42 | MC-BD-C2-1 | 21 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
ZSC-1022 | XV-1022 | On/off shutdown valve | H-101 main fuel gas SSOV - Closed limit switch | AIC-1022 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 18 | FAR-100/SMC-BMS-H101-D01 | TB01-35/36 | JB-BD-C2-1 | 43/44 | MC-BD-C2-1 | 22 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
ZSC-1026 | XV-1026 | On/off shutdown valve | H-101 pilot gas SSOV - Closed limit switch | XV-1026 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 19 | FAR-100/SMC-BMS-H101-D01 | TB01-37/38 | JB-BD-C2-1 | 45/46 | MC-BD-C2-1 | 23 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
ZSC-1230 | XV-1230 | On/off shutdown valve | H-101 FG double block & bleed vent - Closed limit switch | XV-1230 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 20 | FAR-100/SMC-BMS-H101-D01 | TB01-39/40 | JB-BD-C2-1 | 47/48 | MC-BD-C2-1 | 24 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
ZSO-1021 | XV-1021 | On/off shutdown valve | H-101 main fuel gas SSOV - Open limit switch | PIC-1021 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 21 | FAR-100/SMC-BMS-H101-D01 | TB01-41/42 | JB-BD-C2-2 | 1/2 | MC-BD-C2-2 | 1 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
ZSO-1022 | XV-1022 | On/off shutdown valve | H-101 main fuel gas SSOV - Open limit switch | AIC-1022 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 22 | FAR-100/SMC-BMS-H101-D01 | TB01-43/44 | JB-BD-C2-2 | 3/4 | MC-BD-C2-2 | 2 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
ZSO-1026 | XV-1026 | On/off shutdown valve | H-101 pilot gas SSOV - Open limit switch | XV-1026 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 23 | FAR-100/SMC-BMS-H101-D01 | TB01-45/46 | JB-BD-C2-2 | 5/6 | MC-BD-C2-2 | 3 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
ZSO-1230 | XV-1230 | On/off shutdown valve | H-101 FG double block & bleed vent - Open limit switch | XV-1230 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DI | 24 VDC dry contact / NAMUR | BMS-H101-DI01 | 24 | FAR-100/SMC-BMS-H101-D01 | TB01-47/48 | JB-BD-C2-2 | 7/8 | MC-BD-C2-2 | 4 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
XV-1021 | XV-1021 | On/off shutdown valve | H-101 main fuel gas SSOV - SOV de-energise to trip | PIC-1021 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DO | 24 VDC, de-energise to trip | BMS-H101-DO01 | 1 | FAR-100/SMC-BMS-H101-D01 | TB01-1/2 | JB-BD-C2-1 | 33/34 | MC-BD-C2-1 | 17 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
XV-1022 | XV-1022 | On/off shutdown valve | H-101 main fuel gas SSOV - SOV de-energise to trip | AIC-1022 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DO | 24 VDC, de-energise to trip | BMS-H101-DO01 | 2 | FAR-100/SMC-BMS-H101-D01 | TB01-3/4 | JB-BD-C2-1 | 35/36 | MC-BD-C2-1 | 18 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
XV-1026 | XV-1026 | On/off shutdown valve | H-101 pilot gas SSOV - SOV de-energise to trip | XV-1026 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DO | 24 VDC, de-energise to trip | BMS-H101-DO01 | 3 | FAR-100/SMC-BMS-H101-D01 | TB01-5/6 | JB-BD-C2-1 | 37/38 | MC-BD-C2-1 | 19 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
XV-1230 | XV-1230 | On/off shutdown valve | H-101 FG double block & bleed vent - SOV de-energise to trip | XV-1230 | CFU-100-PR-PID-005 | BMS | BMS-H101 | DO | 24 VDC, de-energise to trip | BMS-H101-DO01 | 4 | FAR-100/SMC-BMS-H101-D01 | TB01-7/8 | JB-BD-C2-1 | 39/40 | MC-BD-C2-1 | 20 | 100 | C2 | H-101 | SIF-101 | SIL 2 |  |  | instrument index
FT-2001A | FT-2001A | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2001 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 1 | FAR-100/SMC-BMS-H201-A01 | TB01-1/2 | JB-BA-E2 | 1/2 | MC-BA-E2 | 1 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2001B | FT-2001B | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2001 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 2 | FAR-100/SMC-BMS-H201-A01 | TB01-3/4 | JB-BA-E2 | 3/4 | MC-BA-E2 | 2 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2001C | FT-2001C | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2001 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 3 | FAR-100/SMC-BMS-H201-A01 | TB01-5/6 | JB-BA-E2 | 5/6 | MC-BA-E2 | 3 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2002A | FT-2002A | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2002 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 4 | FAR-100/SMC-BMS-H201-A01 | TB01-7/8 | JB-BA-E2 | 7/8 | MC-BA-E2 | 4 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2002B | FT-2002B | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2002 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 5 | FAR-100/SMC-BMS-H201-A01 | TB01-9/10 | JB-BA-E2 | 9/10 | MC-BA-E2 | 5 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2002C | FT-2002C | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2002 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 6 | FAR-100/SMC-BMS-H201-A01 | TB01-11/12 | JB-BA-E2 | 11/12 | MC-BA-E2 | 6 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2003A | FT-2003A | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2003 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 7 | FAR-100/SMC-BMS-H201-A01 | TB01-13/14 | JB-BA-E2 | 13/14 | MC-BA-E2 | 7 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2003B | FT-2003B | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2003 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 8 | FAR-100/SMC-BMS-H201-A01 | TB01-15/16 | JB-BA-E2 | 15/16 | MC-BA-E2 | 8 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2003C | FT-2003C | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2003 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 9 | FAR-100/SMC-BMS-H201-A01 | TB01-17/18 | JB-BA-E2 | 17/18 | MC-BA-E2 | 9 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2004A | FT-2004A | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2004 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 10 | FAR-100/SMC-BMS-H201-A01 | TB01-19/20 | JB-BA-E2 | 19/20 | MC-BA-E2 | 10 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2004B | FT-2004B | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2004 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 11 | FAR-100/SMC-BMS-H201-A01 | TB01-21/22 | JB-BA-E2 | 21/22 | MC-BA-E2 | 11 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
FT-2004C | FT-2004C | Flow transmitter | H-201 low-low pass flow -> trip fuel | FIC-2004 | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 12 | FAR-100/SMC-BMS-H201-A01 | TB01-23/24 | JB-BA-E2 | 23/24 | MC-BA-E2 | 12 | 190 | E2 | H-201 | SIF-201 | SIL 2 | 0-120 | m3/h | instrument index
PT-2009A | PT-2009A | Pressure transmitter | H-201 low-low FG pressure / flame failure -> trip | PT-2009A | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI01 | 13 | FAR-100/SMC-BMS-H201-A01 | TB01-25/26 | JB-BA-E2 | 25/26 | MC-BA-E2 | 13 | 190 | E2 | H-201 | SIF-202 | SIL 1 | 0-5 | barg | instrument index
PT-2009B | PT-2009B | Pressure transmitter | H-201 low-low FG pressure / flame failure -> trip | PT-2009B | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI02 | 1 | FAR-100/SMC-BMS-H201-A01 | TB02-1/2 | JB-BA-E2 | 27/28 | MC-BA-E2 | 14 | 190 | E2 | H-201 | SIF-202 | SIL 1 | 0-5 | barg | instrument index
PT-2009C | PT-2009C | Pressure transmitter | H-201 low-low FG pressure / flame failure -> trip | PT-2009C | CFU-200-PR-PID-012 | BMS | BMS-H201 | AI | 4-20 mA HART, 2-wire, IS (Ex ia) | BMS-H201-AI02 | 2 | FAR-100/SMC-BMS-H201-A01 | TB02-3/4 | JB-BA-E2 | 29/30 | MC-BA-E2 | 15 | 190 | E2 | H-201 | SIF-202 | SIL 1 | 0-5 | barg | instrument index
BS-2008-01 | BS-2008 | Flame scanner | H-201 flame scanners (1 per burner) - Flame scanner burner 1 (flame on) | AIC-2008 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 1 | FAR-100/SMC-BMS-H201-D01 | TB01-1/2 | JB-BD-E2 | 1/2 | MC-BD-E2 | 1 | 190 | E2 | H-201 |  |  | Flame ON/OFF | - | instrument index
BS-2008-02 | BS-2008 | Flame scanner | H-201 flame scanners (1 per burner) - Flame scanner burner 2 (flame on) | AIC-2008 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 2 | FAR-100/SMC-BMS-H201-D01 | TB01-3/4 | JB-BD-E2 | 3/4 | MC-BD-E2 | 2 | 190 | E2 | H-201 |  |  | Flame ON/OFF | - | instrument index
BS-2008-03 | BS-2008 | Flame scanner | H-201 flame scanners (1 per burner) - Flame scanner burner 3 (flame on) | AIC-2008 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 3 | FAR-100/SMC-BMS-H201-D01 | TB01-5/6 | JB-BD-E2 | 5/6 | MC-BD-E2 | 3 | 190 | E2 | H-201 |  |  | Flame ON/OFF | - | instrument index
BS-2008-04 | BS-2008 | Flame scanner | H-201 flame scanners (1 per burner) - Flame scanner burner 4 (flame on) | AIC-2008 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 4 | FAR-100/SMC-BMS-H201-D01 | TB01-7/8 | JB-BD-E2 | 7/8 | MC-BD-E2 | 4 | 190 | E2 | H-201 |  |  | Flame ON/OFF | - | instrument index
BS-2008-05 | BS-2008 | Flame scanner | H-201 flame scanners (1 per burner) - Flame scanner burner 5 (flame on) | AIC-2008 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 5 | FAR-100/SMC-BMS-H201-D01 | TB01-9/10 | JB-BD-E2 | 9/10 | MC-BD-E2 | 5 | 190 | E2 | H-201 |  |  | Flame ON/OFF | - | instrument index
BS-2008-06 | BS-2008 | Flame scanner | H-201 flame scanners (1 per burner) - Flame scanner burner 6 (flame on) | AIC-2008 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 6 | FAR-100/SMC-BMS-H201-D01 | TB01-11/12 | JB-BD-E2 | 11/12 | MC-BD-E2 | 6 | 190 | E2 | H-201 |  |  | Flame ON/OFF | - | instrument index
ZSC-2006A | XV-2006A | On/off shutdown valve | H-201 fuel gas SSOV - Closed limit switch | PIC-2006 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 7 | FAR-100/SMC-BMS-H201-D01 | TB01-13/14 | JB-BD-E2 | 19/20 | MC-BD-E2 | 10 | 190 | E2 | H-201 | SIF-201 | SIL 2 |  |  | instrument index
ZSC-2006B | XV-2006B | On/off shutdown valve | H-201 fuel gas SSOV - Closed limit switch | PIC-2006 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 8 | FAR-100/SMC-BMS-H201-D01 | TB01-15/16 | JB-BD-E2 | 21/22 | MC-BD-E2 | 11 | 190 | E2 | H-201 | SIF-201 | SIL 2 |  |  | instrument index
ZSC-2105 | XV-2105 | On/off shutdown valve | H-201 FG double block & bleed vent - Closed limit switch | XV-2105 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 9 | FAR-100/SMC-BMS-H201-D01 | TB01-17/18 | JB-BD-E2 | 23/24 | MC-BD-E2 | 12 | 190 | E2 | H-201 | SIF-201 | SIL 2 |  |  | instrument index
ZSO-2006A | XV-2006A | On/off shutdown valve | H-201 fuel gas SSOV - Open limit switch | PIC-2006 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 10 | FAR-100/SMC-BMS-H201-D01 | TB01-19/20 | JB-BD-E2 | 25/26 | MC-BD-E2 | 13 | 190 | E2 | H-201 | SIF-201 | SIL 2 |  |  | instrument index
ZSO-2006B | XV-2006B | On/off shutdown valve | H-201 fuel gas SSOV - Open limit switch | PIC-2006 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 11 | FAR-100/SMC-BMS-H201-D01 | TB01-21/22 | JB-BD-E2 | 27/28 | MC-BD-E2 | 14 | 190 | E2 | H-201 | SIF-201 | SIL 2 |  |  | instrument index
ZSO-2105 | XV-2105 | On/off shutdown valve | H-201 FG double block & bleed vent - Open limit switch | XV-2105 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DI | 24 VDC dry contact / NAMUR | BMS-H201-DI01 | 12 | FAR-100/SMC-BMS-H201-D01 | TB01-23/24 | JB-BD-E2 | 29/30 | MC-BD-E2 | 15 | 190 | E2 | H-201 | SIF-201 | SIL 2 |  |  | instrument index
XV-2006A | XV-2006A | On/off shutdown valve | H-201 fuel gas SSOV - SOV de-energise to trip | PIC-2006 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DO | 24 VDC, de-energise to trip | BMS-H201-DO01 | 1 | FAR-100/SMC-BMS-H201-D01 | TB01-1/2 | JB-BD-E2 | 13/14 | MC-BD-E2 | 7 | 190 | E2 | H-201 | SIF-201 | SIL 2 |  |  | instrument index
XV-2006B | XV-2006B | On/off shutdown valve | H-201 fuel gas SSOV - SOV de-energise to trip | PIC-2006 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DO | 24 VDC, de-energise to trip | BMS-H201-DO01 | 2 | FAR-100/SMC-BMS-H201-D01 | TB01-3/4 | JB-BD-E2 | 15/16 | MC-BD-E2 | 8 | 190 | E2 | H-201 | SIF-201 | SIL 2 |  |  | instrument index
XV-2105 | XV-2105 | On/off shutdown valve | H-201 FG double block & bleed vent - SOV de-energise to trip | XV-2105 | CFU-200-PR-PID-012 | BMS | BMS-H201 | DO | 24 VDC, de-energise to trip | BMS-H201-DO01 | 3 | FAR-100/SMC-BMS-H201-D01 | TB01-5/6 | JB-BD-E2 | 17/18 | MC-BD-E2 | 9 | 190 | E2 | H-201 | SIF-201 | SIL 2 |  |  | instrument index
BD-0101 | FZ-01 | Flame detector (IR3) | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 1 | FAR-100/FMC-FGS-1-A01 | TB01-1/2 | JB-FA-A2 | 1/2 | MC-FA-A2 | 1 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0102 | FZ-01 | Flame detector (IR3) | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 2 | FAR-100/FMC-FGS-1-A01 | TB01-3/4 | JB-FA-A2 | 3/4 | MC-FA-A2 | 2 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0101 | FZ-01 | Flammable gas detector (IR point) | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 3 | FAR-100/FMC-FGS-1-A01 | TB01-5/6 | JB-FA-A2 | 5/6 | MC-FA-A2 | 3 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0102 | FZ-01 | Flammable gas detector (IR point) | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 4 | FAR-100/FMC-FGS-1-A01 | TB01-7/8 | JB-FA-A2 | 7/8 | MC-FA-A2 | 4 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0103 | FZ-01 | Flammable gas detector (IR point) | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 5 | FAR-100/FMC-FGS-1-A01 | TB01-9/10 | JB-FA-A2 | 9/10 | MC-FA-A2 | 5 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0104 | FZ-01 | Flammable gas detector (IR point) | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 6 | FAR-100/FMC-FGS-1-A01 | TB01-11/12 | JB-FA-A2 | 11/12 | MC-FA-A2 | 6 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0105 | FZ-01 | Flammable gas detector (IR point) | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 7 | FAR-100/FMC-FGS-1-A01 | TB01-13/14 | JB-FA-A2 | 13/14 | MC-FA-A2 | 7 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0106 | FZ-01 | Flammable gas detector (IR point) | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 8 | FAR-100/FMC-FGS-1-A01 | TB01-15/16 | JB-FA-A2 | 15/16 | MC-FA-A2 | 8 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-1501 | GD-1501 | Gas detector | Flammable gas detector (IR point), pump row P-101A/B | GD-1501 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 9 | FAR-100/FMC-FGS-1-A01 | TB01-17/18 | JB-FA-A3 | 1/2 | MC-FA-A3 | 1 | 160 | A3 | P-101A |  |  | 0-100 | % LEL | instrument index
GD-1513 | GD-1513 | Gas detector | Flammable gas detector (IR point), pump row P-114A/B | GD-1513 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 10 | FAR-100/FMC-FGS-1-A01 | TB01-19/20 | JB-FA-A3 | 3/4 | MC-FA-A3 | 2 | 120 | A3 | P-114A |  |  | 0-100 | % LEL | instrument index
GD-1517 | GD-1517 | Gas detector | Flammable gas detector (IR point), pump row P-118A/B | GD-1517 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 11 | FAR-100/FMC-FGS-1-A01 | TB01-21/22 | JB-FA-A3 | 5/6 | MC-FA-A3 | 3 | 110 | A3 | P-118 |  |  | 0-100 | % LEL | instrument index
BD-0201 | FZ-02 | Flame detector (IR3) | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 12 | FAR-100/FMC-FGS-1-A01 | TB01-23/24 | JB-FA-A4 | 1/2 | MC-FA-A4 | 1 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0202 | FZ-02 | Flame detector (IR3) | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI01 | 13 | FAR-100/FMC-FGS-1-A01 | TB01-25/26 | JB-FA-A4 | 3/4 | MC-FA-A4 | 2 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0203 | FZ-02 | Flame detector (IR3) | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 1 | FAR-100/FMC-FGS-1-A01 | TB02-1/2 | JB-FA-A4 | 5/6 | MC-FA-A4 | 3 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0201 | FZ-02 | Flammable gas detector (IR point) | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 2 | FAR-100/FMC-FGS-1-A01 | TB02-3/4 | JB-FA-A4 | 7/8 | MC-FA-A4 | 4 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0202 | FZ-02 | Flammable gas detector (IR point) | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 3 | FAR-100/FMC-FGS-1-A01 | TB02-5/6 | JB-FA-A4 | 9/10 | MC-FA-A4 | 5 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0203 | FZ-02 | Flammable gas detector (IR point) | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 4 | FAR-100/FMC-FGS-1-A01 | TB02-7/8 | JB-FA-A4 | 11/12 | MC-FA-A4 | 6 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0204 | FZ-02 | Flammable gas detector (IR point) | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 5 | FAR-100/FMC-FGS-1-A01 | TB02-9/10 | JB-FA-A4 | 13/14 | MC-FA-A4 | 7 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0205 | FZ-02 | Flammable gas detector (IR point) | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 6 | FAR-100/FMC-FGS-1-A01 | TB02-11/12 | JB-FA-A4 | 15/16 | MC-FA-A4 | 8 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0206 | FZ-02 | Flammable gas detector (IR point) | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 7 | FAR-100/FMC-FGS-1-A01 | TB02-13/14 | JB-FA-A4 | 17/18 | MC-FA-A4 | 9 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-1285 | GD-1285 | Gas detector | Flammable gas detector, LPG pump area P-115 (1) | GD-1285 | CFU-100-PR-PID-010 | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 8 | FAR-100/FMC-FGS-1-A01 | TB02-15/16 | JB-FA-B3 | 1/2 | MC-FA-B3 | 1 | 120 | B3 | P-115A |  |  | 0-100 | % LEL | instrument index
GD-1286 | GD-1286 | Gas detector | Flammable gas detector, LPG pump area P-115 (2) | GD-1286 | CFU-100-PR-PID-010 | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 9 | FAR-100/FMC-FGS-1-A01 | TB02-17/18 | JB-FA-B3 | 3/4 | MC-FA-B3 | 2 | 120 | B3 | P-115A |  |  | 0-100 | % LEL | instrument index
GD-1502 | GD-1502 | Gas detector | Flammable gas detector (IR point), pump row P-102A/B | GD-1502 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 10 | FAR-100/FMC-FGS-1-A01 | TB02-19/20 | JB-FA-B3 | 5/6 | MC-FA-B3 | 3 | 100 | B3 | P-102A |  |  | 0-100 | % LEL | instrument index
GD-1503 | GD-1503 | Gas detector | Flammable gas detector (IR point), pump row P-103A/B | GD-1503 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 11 | FAR-100/FMC-FGS-1-A01 | TB02-21/22 | JB-FA-B3 | 7/8 | MC-FA-B3 | 4 | 130 | B3 | P-103A |  |  | 0-100 | % LEL | instrument index
GD-1504 | GD-1504 | Gas detector | Flammable gas detector (IR point), pump row P-104A/B | GD-1504 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 12 | FAR-100/FMC-FGS-1-A01 | TB02-23/24 | JB-FA-B3 | 9/10 | MC-FA-B3 | 5 | 140 | B3 | P-104A |  |  | 0-100 | % LEL | instrument index
GD-1514 | GD-1514 | Gas detector | Flammable gas detector (IR point), pump row P-115A/B | GD-1514 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI02 | 13 | FAR-100/FMC-FGS-1-A01 | TB02-25/26 | JB-FA-B3 | 11/12 | MC-FA-B3 | 6 | 120 | B3 | P-115A |  |  | 0-100 | % LEL | instrument index
GD-1515 | GD-1515 | Gas detector | Flammable gas detector (IR point), pump row P-116A/B | GD-1515 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 1 | FAR-100/FMC-FGS-1-A01 | TB03-1/2 | JB-FA-B3 | 13/14 | MC-FA-B3 | 7 | 110 | B3 | P-116A |  |  | 0-100 | % LEL | instrument index
GD-1516 | GD-1516 | Gas detector | Flammable gas detector (IR point), pump row P-117A/B | GD-1516 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 2 | FAR-100/FMC-FGS-1-A01 | TB03-3/4 | JB-FA-B3 | 15/16 | MC-FA-B3 | 8 | 110 | B3 | P-117A |  |  | 0-100 | % LEL | instrument index
AT-0401 | FZ-04 | H2S detector | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 3 | FAR-100/FMC-FGS-1-A01 | TB03-5/6 | JB-FA-B4 | 1/2 | MC-FA-B4 | 1 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
AT-0402 | FZ-04 | H2S detector | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 4 | FAR-100/FMC-FGS-1-A01 | TB03-7/8 | JB-FA-B4 | 3/4 | MC-FA-B4 | 2 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0401 | FZ-04 | Flame detector (IR3) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 5 | FAR-100/FMC-FGS-1-A01 | TB03-9/10 | JB-FA-B4 | 5/6 | MC-FA-B4 | 3 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0402 | FZ-04 | Flame detector (IR3) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 6 | FAR-100/FMC-FGS-1-A01 | TB03-11/12 | JB-FA-B4 | 7/8 | MC-FA-B4 | 4 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0403 | FZ-04 | Flame detector (IR3) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 7 | FAR-100/FMC-FGS-1-A01 | TB03-13/14 | JB-FA-B4 | 9/10 | MC-FA-B4 | 5 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0401 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 8 | FAR-100/FMC-FGS-1-A01 | TB03-15/16 | JB-FA-B4 | 11/12 | MC-FA-B4 | 6 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0402 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 9 | FAR-100/FMC-FGS-1-A01 | TB03-17/18 | JB-FA-B4 | 13/14 | MC-FA-B4 | 7 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0403 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 10 | FAR-100/FMC-FGS-1-A01 | TB03-19/20 | JB-FA-B4 | 15/16 | MC-FA-B4 | 8 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0404 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 11 | FAR-100/FMC-FGS-1-A01 | TB03-21/22 | JB-FA-B4 | 17/18 | MC-FA-B4 | 9 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0405 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 12 | FAR-100/FMC-FGS-1-A01 | TB03-23/24 | JB-FA-B4 | 19/20 | MC-FA-B4 | 10 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0406 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI03 | 13 | FAR-100/FMC-FGS-1-A01 | TB03-25/26 | JB-FA-B4 | 21/22 | MC-FA-B4 | 11 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0407 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 1 | FAR-100/FMC-FGS-1-A01 | TB04-1/2 | JB-FA-B4 | 23/24 | MC-FA-B4 | 12 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0408 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 2 | FAR-100/FMC-FGS-1-A01 | TB04-3/4 | JB-FA-B4 | 25/26 | MC-FA-B4 | 13 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0409 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 3 | FAR-100/FMC-FGS-1-A01 | TB04-5/6 | JB-FA-B4 | 27/28 | MC-FA-B4 | 14 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0410 | FZ-04 | Flammable gas detector (IR point) | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 4 | FAR-100/FMC-FGS-1-A01 | TB04-7/8 | JB-FA-B4 | 29/30 | MC-FA-B4 | 15 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-1522 | GD-1522 | Gas detector | Flammable gas detector (IR point), LPG / light-ends area at C-105 | GD-1522 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 5 | FAR-100/FMC-FGS-1-A01 | TB04-9/10 | JB-FA-B4 | 31/32 | MC-FA-B4 | 16 | 140 | B4 | C-105 |  |  | 0-100 | % LEL | instrument index
GD-1523 | GD-1523 | Gas detector | Flammable gas detector (IR point), LPG / light-ends area at D-105 | GD-1523 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 6 | FAR-100/FMC-FGS-1-A01 | TB04-11/12 | JB-FA-B4 | 33/34 | MC-FA-B4 | 17 | 130 | B4 | D-105 |  |  | 0-100 | % LEL | instrument index
GD-1524 | GD-1524 | Gas detector | Flammable gas detector (IR point), LPG / light-ends area at C-106 | GD-1524 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 7 | FAR-100/FMC-FGS-1-A01 | TB04-13/14 | JB-FA-B4 | 35/36 | MC-FA-B4 | 18 | 130 | B4 | C-106 |  |  | 0-100 | % LEL | instrument index
GD-1525 | GD-1525 | Gas detector | Flammable gas detector (IR point), LPG / light-ends area at D-106 | GD-1525 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 8 | FAR-100/FMC-FGS-1-A01 | TB04-15/16 | JB-FA-B4 | 37/38 | MC-FA-B4 | 19 | 120 | B4 | D-106 |  |  | 0-100 | % LEL | instrument index
GD-1526 | GD-1526 | Gas detector | Flammable gas detector (IR point), LPG / light-ends area at E-116 | GD-1526 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 9 | FAR-100/FMC-FGS-1-A01 | TB04-17/18 | JB-FA-B4 | 39/40 | MC-FA-B4 | 20 | 140 | B4 | E-116 |  |  | 0-100 | % LEL | instrument index
GD-1527 | GD-1527 | Gas detector | Flammable gas detector (IR point), D-102 overhead drum (1) | GD-1527 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 10 | FAR-100/FMC-FGS-1-A01 | TB04-19/20 | JB-FA-B4 | 41/42 | MC-FA-B4 | 21 | 140 | B4 | D-102 |  |  | 0-100 | % LEL | instrument index
GD-1528 | GD-1528 | Gas detector | Flammable gas detector (IR point), D-102 overhead drum (2) | GD-1528 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 11 | FAR-100/FMC-FGS-1-A01 | TB04-21/22 | JB-FA-B4 | 43/44 | MC-FA-B4 | 22 | 140 | B4 | D-102 |  |  | 0-100 | % LEL | instrument index
GD-1529 | GD-1529 | Gas detector | H2S toxic gas detector (electrochemical), D-102 (1) | GD-1529 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 12 | FAR-100/FMC-FGS-1-A01 | TB04-23/24 | JB-FA-B4 | 45/46 | MC-FA-B4 | 23 | 140 | B4 | D-102 |  |  | 0-50 | ppm H2S | instrument index
GD-1530 | GD-1530 | Gas detector | H2S toxic gas detector (electrochemical), D-102 (2) | GD-1530 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI04 | 13 | FAR-100/FMC-FGS-1-A01 | TB04-25/26 | JB-FA-B4 | 47/48 | MC-FA-B4 | 24 | 140 | B4 | D-102 |  |  | 0-50 | ppm H2S | instrument index
BE-1532 | BE-1532 | Flame detector (F&G) | Flame detector (IR3), H-101 burner front / FG train (1) | BE-1532 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 1 | FAR-100/FMC-FGS-1-A01 | TB05-1/2 | JB-FA-C2 | 1/2 | MC-FA-C2 | 1 | 100 | C2 | H-101 |  |  | Fire / no fire | - | instrument index
BE-1533 | BE-1533 | Flame detector (F&G) | Flame detector (IR3), H-101 burner front / FG train (2) | BE-1533 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 2 | FAR-100/FMC-FGS-1-A01 | TB05-3/4 | JB-FA-C2 | 3/4 | MC-FA-C2 | 2 | 100 | C2 | H-101 |  |  | Fire / no fire | - | instrument index
BE-1534 | BE-1534 | Flame detector (F&G) | Flame detector (IR3), H-101 burner front / FG train (3) | BE-1534 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 3 | FAR-100/FMC-FGS-1-A01 | TB05-5/6 | JB-FA-C2 | 5/6 | MC-FA-C2 | 3 | 100 | C2 | H-101 |  |  | Fire / no fire | - | instrument index
BE-1535 | BE-1535 | Flame detector (F&G) | Flame detector (IR3), H-101 burner front / FG train (4) | BE-1535 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 4 | FAR-100/FMC-FGS-1-A01 | TB05-7/8 | JB-FA-C2 | 7/8 | MC-FA-C2 | 4 | 100 | C2 | H-101 |  |  | Fire / no fire | - | instrument index
GD-1520 | GD-1520 | Gas detector | Flammable gas detector (catalytic), H-101 FG train | GD-1520 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 5 | FAR-100/FMC-FGS-1-A01 | TB05-9/10 | JB-FA-C2 | 9/10 | MC-FA-C2 | 5 | 100 | C2 | H-101 |  |  | 0-100 | % LEL | instrument index
GD-1521 | GD-1521 | Gas detector | Flammable gas detector (catalytic), H-101 burner manifold | GD-1521 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 6 | FAR-100/FMC-FGS-1-A01 | TB05-11/12 | JB-FA-C2 | 11/12 | MC-FA-C2 | 6 | 100 | C2 | H-101 |  |  | 0-100 | % LEL | instrument index
BE-1536 | BE-1536 | Flame detector (F&G) | Flame detector (IR3), hot pump P-112A/B | BE-1536 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 7 | FAR-100/FMC-FGS-1-A01 | TB05-13/14 | JB-FA-C3 | 1/2 | MC-FA-C3 | 1 | 150 | C3 | P-112A |  |  | Fire / no fire | - | instrument index
BE-1537 | BE-1537 | Flame detector (F&G) | Flame detector (IR3), hot pump P-108A/B | BE-1537 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 8 | FAR-100/FMC-FGS-1-A01 | TB05-15/16 | JB-FA-C3 | 3/4 | MC-FA-C3 | 2 | 160 | C3 | P-108A |  |  | Fire / no fire | - | instrument index
BE-1538 | BE-1538 | Flame detector (F&G) | Flame detector (IR3), hot pump P-111A/B | BE-1538 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 9 | FAR-100/FMC-FGS-1-A01 | TB05-17/18 | JB-FA-C3 | 5/6 | MC-FA-C3 | 3 | 180 | C3 | P-111A |  |  | Fire / no fire | - | instrument index
BE-1539 | BE-1539 | Flame detector (F&G) | Flame detector (IR3), hot pump P-110A/B | BE-1539 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 10 | FAR-100/FMC-FGS-1-A01 | TB05-19/20 | JB-FA-C3 | 7/8 | MC-FA-C3 | 4 | 170 | C3 | P-110A |  |  | Fire / no fire | - | instrument index
GD-1505 | GD-1505 | Gas detector | Flammable gas detector (IR point), pump row P-105A/B | GD-1505 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 11 | FAR-100/FMC-FGS-1-A01 | TB05-21/22 | JB-FA-C3 | 9/10 | MC-FA-C3 | 5 | 140 | C3 | P-105A |  |  | 0-100 | % LEL | instrument index
GD-1508 | GD-1508 | Gas detector | Flammable gas detector (IR point), pump row P-108A/B | GD-1508 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 12 | FAR-100/FMC-FGS-1-A01 | TB05-23/24 | JB-FA-C3 | 11/12 | MC-FA-C3 | 6 | 160 | C3 | P-108A |  |  | 0-100 | % LEL | instrument index
GD-1509 | GD-1509 | Gas detector | Flammable gas detector (IR point), pump row P-109A/B | GD-1509 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI05 | 13 | FAR-100/FMC-FGS-1-A01 | TB05-25/26 | JB-FA-C3 | 13/14 | MC-FA-C3 | 7 | 170 | C3 | P-109A |  |  | 0-100 | % LEL | instrument index
GD-1510 | GD-1510 | Gas detector | Flammable gas detector (IR point), pump row P-110A/B | GD-1510 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 1 | FAR-100/FMC-FGS-1-A01 | TB06-1/2 | JB-FA-C3 | 15/16 | MC-FA-C3 | 8 | 170 | C3 | P-110A |  |  | 0-100 | % LEL | instrument index
GD-1511 | GD-1511 | Gas detector | Flammable gas detector (IR point), pump row P-111A/B | GD-1511 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 2 | FAR-100/FMC-FGS-1-A01 | TB06-3/4 | JB-FA-C3 | 17/18 | MC-FA-C3 | 9 | 180 | C3 | P-111A |  |  | 0-100 | % LEL | instrument index
GD-1512 | GD-1512 | Gas detector | Flammable gas detector (IR point), pump row P-112A/B | GD-1512 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 3 | FAR-100/FMC-FGS-1-A01 | TB06-5/6 | JB-FA-C3 | 19/20 | MC-FA-C3 | 10 | 150 | C3 | P-112A |  |  | 0-100 | % LEL | instrument index
GD-1531 | GD-1531 | Gas detector | H2S toxic gas detector (electrochemical), P-105 | GD-1531 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 4 | FAR-100/FMC-FGS-1-A01 | TB06-7/8 | JB-FA-C3 | 21/22 | MC-FA-C3 | 11 | 140 | C3 | P-105A |  |  | 0-50 | ppm H2S | instrument index
AT-0301 | FZ-03 | H2S detector | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 5 | FAR-100/FMC-FGS-1-A01 | TB06-9/10 | JB-FA-C4 | 1/2 | MC-FA-C4 | 1 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
AT-0302 | FZ-03 | H2S detector | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 6 | FAR-100/FMC-FGS-1-A01 | TB06-11/12 | JB-FA-C4 | 3/4 | MC-FA-C4 | 2 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
AT-0303 | FZ-03 | H2S detector | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 7 | FAR-100/FMC-FGS-1-A01 | TB06-13/14 | JB-FA-C4 | 5/6 | MC-FA-C4 | 3 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
AT-0304 | FZ-03 | H2S detector | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 8 | FAR-100/FMC-FGS-1-A01 | TB06-15/16 | JB-FA-C4 | 7/8 | MC-FA-C4 | 4 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0301 | FZ-03 | Flame detector (IR3) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 9 | FAR-100/FMC-FGS-1-A01 | TB06-17/18 | JB-FA-C4 | 9/10 | MC-FA-C4 | 5 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0302 | FZ-03 | Flame detector (IR3) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 10 | FAR-100/FMC-FGS-1-A01 | TB06-19/20 | JB-FA-C4 | 11/12 | MC-FA-C4 | 6 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0303 | FZ-03 | Flame detector (IR3) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 11 | FAR-100/FMC-FGS-1-A01 | TB06-21/22 | JB-FA-C4 | 13/14 | MC-FA-C4 | 7 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0304 | FZ-03 | Flame detector (IR3) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 12 | FAR-100/FMC-FGS-1-A01 | TB06-23/24 | JB-FA-C4 | 15/16 | MC-FA-C4 | 8 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0301 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI06 | 13 | FAR-100/FMC-FGS-1-A01 | TB06-25/26 | JB-FA-C4 | 17/18 | MC-FA-C4 | 9 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0302 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 1 | FAR-100/FMC-FGS-1-A01 | TB07-1/2 | JB-FA-C4 | 19/20 | MC-FA-C4 | 10 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0303 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 2 | FAR-100/FMC-FGS-1-A01 | TB07-3/4 | JB-FA-C4 | 21/22 | MC-FA-C4 | 11 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0304 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 3 | FAR-100/FMC-FGS-1-A01 | TB07-5/6 | JB-FA-C4 | 23/24 | MC-FA-C4 | 12 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0305 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 4 | FAR-100/FMC-FGS-1-A01 | TB07-7/8 | JB-FA-C4 | 25/26 | MC-FA-C4 | 13 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0306 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 5 | FAR-100/FMC-FGS-1-A01 | TB07-9/10 | JB-FA-C4 | 27/28 | MC-FA-C4 | 14 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0307 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 6 | FAR-100/FMC-FGS-1-A01 | TB07-11/12 | JB-FA-C4 | 29/30 | MC-FA-C4 | 15 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0308 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 7 | FAR-100/FMC-FGS-1-A01 | TB07-13/14 | JB-FA-C4 | 31/32 | MC-FA-C4 | 16 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0309 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 8 | FAR-100/FMC-FGS-1-A01 | TB07-15/16 | JB-FA-C4 | 33/34 | MC-FA-C4 | 17 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0310 | FZ-03 | Flammable gas detector (IR point) | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 9 | FAR-100/FMC-FGS-1-A01 | TB07-17/18 | JB-FA-C4 | 35/36 | MC-FA-C4 | 18 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0501 | FZ-05 | Flame detector (IR3) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 10 | FAR-100/FMC-FGS-1-A01 | TB07-19/20 | JB-FA-D2 | 1/2 | MC-FA-D2 | 1 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0502 | FZ-05 | Flame detector (IR3) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 11 | FAR-100/FMC-FGS-1-A01 | TB07-21/22 | JB-FA-D2 | 3/4 | MC-FA-D2 | 2 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0503 | FZ-05 | Flame detector (IR3) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 12 | FAR-100/FMC-FGS-1-A01 | TB07-23/24 | JB-FA-D2 | 5/6 | MC-FA-D2 | 3 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0504 | FZ-05 | Flame detector (IR3) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI07 | 13 | FAR-100/FMC-FGS-1-A01 | TB07-25/26 | JB-FA-D2 | 7/8 | MC-FA-D2 | 4 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0501 | FZ-05 | Flammable gas detector (IR point) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 1 | FAR-100/FMC-FGS-1-A01 | TB08-1/2 | JB-FA-D2 | 9/10 | MC-FA-D2 | 5 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0502 | FZ-05 | Flammable gas detector (IR point) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 2 | FAR-100/FMC-FGS-1-A01 | TB08-3/4 | JB-FA-D2 | 11/12 | MC-FA-D2 | 6 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0503 | FZ-05 | Flammable gas detector (IR point) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 3 | FAR-100/FMC-FGS-1-A01 | TB08-5/6 | JB-FA-D2 | 13/14 | MC-FA-D2 | 7 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0504 | FZ-05 | Flammable gas detector (IR point) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 4 | FAR-100/FMC-FGS-1-A01 | TB08-7/8 | JB-FA-D2 | 15/16 | MC-FA-D2 | 8 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0505 | FZ-05 | Flammable gas detector (IR point) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 5 | FAR-100/FMC-FGS-1-A01 | TB08-9/10 | JB-FA-D2 | 17/18 | MC-FA-D2 | 9 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0506 | FZ-05 | Flammable gas detector (IR point) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 6 | FAR-100/FMC-FGS-1-A01 | TB08-11/12 | JB-FA-D2 | 19/20 | MC-FA-D2 | 10 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0507 | FZ-05 | Flammable gas detector (IR point) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 7 | FAR-100/FMC-FGS-1-A01 | TB08-13/14 | JB-FA-D2 | 21/22 | MC-FA-D2 | 11 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0508 | FZ-05 | Flammable gas detector (IR point) | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 8 | FAR-100/FMC-FGS-1-A01 | TB08-15/16 | JB-FA-D2 | 23/24 | MC-FA-D2 | 12 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-1506 | GD-1506 | Gas detector | Flammable gas detector (IR point), pump row P-106A/B | GD-1506 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 9 | FAR-100/FMC-FGS-1-A01 | TB08-17/18 | JB-FA-D3 | 1/2 | MC-FA-D3 | 1 | 190 | D3 | P-106A |  |  | 0-100 | % LEL | instrument index
GD-1507 | GD-1507 | Gas detector | Flammable gas detector (IR point), pump row P-107A/B | GD-1507 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 10 | FAR-100/FMC-FGS-1-A01 | TB08-19/20 | JB-FA-D3 | 3/4 | MC-FA-D3 | 2 | 200 | D3 | P-107A |  |  | 0-100 | % LEL | instrument index
GD-1518 | GD-1518 | Gas detector | Flammable gas detector (IR point), pump row P-119A/B | GD-1518 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 11 | FAR-100/FMC-FGS-1-A01 | TB08-21/22 | JB-FA-D5 | 1/2 | MC-FA-D5 | 1 | 250 | D5 | P-119A |  |  | 0-100 | % LEL | instrument index
GD-1519 | GD-1519 | Gas detector | Flammable gas detector (IR point), pump row P-119A/B | GD-1519 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 12 | FAR-100/FMC-FGS-1-A01 | TB08-23/24 | JB-FA-D5 | 3/4 | MC-FA-D5 | 2 | 250 | D5 | P-119A |  |  | 0-100 | % LEL | instrument index
BE-2513 | BE-2513 | Flame detector (F&G) | Flame detector (IR3), H-201 burner front / FG train (1) | BE-2513 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI08 | 13 | FAR-100/FMC-FGS-1-A01 | TB08-25/26 | JB-FA-E2 | 1/2 | MC-FA-E2 | 1 | 190 | E2 | H-201 |  |  | Fire / no fire | - | instrument index
BE-2514 | BE-2514 | Flame detector (F&G) | Flame detector (IR3), H-201 burner front / FG train (2) | BE-2514 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 1 | FAR-100/FMC-FGS-1-A01 | TB09-1/2 | JB-FA-E2 | 3/4 | MC-FA-E2 | 2 | 190 | E2 | H-201 |  |  | Fire / no fire | - | instrument index
GD-2507 | GD-2507 | Gas detector | Flammable gas detector (catalytic), H-201 FG train | GD-2507 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 2 | FAR-100/FMC-FGS-1-A01 | TB09-3/4 | JB-FA-E2 | 5/6 | MC-FA-E2 | 3 | 190 | E2 | H-201 |  |  | 0-100 | % LEL | instrument index
GD-2508 | GD-2508 | Gas detector | Flammable gas detector (catalytic), H-201 burner manifold | GD-2508 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 3 | FAR-100/FMC-FGS-1-A01 | TB09-5/6 | JB-FA-E2 | 7/8 | MC-FA-E2 | 4 | 190 | E2 | H-201 |  |  | 0-100 | % LEL | instrument index
BE-2515 | BE-2515 | Flame detector (F&G) | Flame detector (IR3), hot pump P-204A/B | BE-2515 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 4 | FAR-100/FMC-FGS-1-A01 | TB09-7/8 | JB-FA-E3 | 1/2 | MC-FA-E3 | 1 | 250 | E3 | P-204A |  |  | Fire / no fire | - | instrument index
BE-2516 | BE-2516 | Flame detector (F&G) | Flame detector (IR3), hot pump P-202A/B | BE-2516 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 5 | FAR-100/FMC-FGS-1-A01 | TB09-9/10 | JB-FA-E3 | 3/4 | MC-FA-E3 | 2 | 260 | E3 | P-202A |  |  | Fire / no fire | - | instrument index
BE-2517 | BE-2517 | Flame detector (F&G) | Flame detector (IR3), hot pump P-203A/B | BE-2517 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 6 | FAR-100/FMC-FGS-1-A01 | TB09-11/12 | JB-FA-E3 | 5/6 | MC-FA-E3 | 3 | 260 | E3 | P-203A |  |  | Fire / no fire | - | instrument index
GD-2501 | GD-2501 | Gas detector | Flammable gas detector (IR point), pump row P-201A/B | GD-2501 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 7 | FAR-100/FMC-FGS-1-A01 | TB09-13/14 | JB-FA-E3 | 7/8 | MC-FA-E3 | 4 | 270 | E3 | P-201A |  |  | 0-100 | % LEL | instrument index
GD-2502 | GD-2502 | Gas detector | Flammable gas detector (IR point), pump row P-202A/B | GD-2502 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 8 | FAR-100/FMC-FGS-1-A01 | TB09-15/16 | JB-FA-E3 | 9/10 | MC-FA-E3 | 5 | 260 | E3 | P-202A |  |  | 0-100 | % LEL | instrument index
GD-2503 | GD-2503 | Gas detector | Flammable gas detector (IR point), pump row P-203A/B | GD-2503 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 9 | FAR-100/FMC-FGS-1-A01 | TB09-17/18 | JB-FA-E3 | 11/12 | MC-FA-E3 | 6 | 260 | E3 | P-203A |  |  | 0-100 | % LEL | instrument index
GD-2504 | GD-2504 | Gas detector | Flammable gas detector (IR point), pump row P-204A/B | GD-2504 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 10 | FAR-100/FMC-FGS-1-A01 | TB09-19/20 | JB-FA-E3 | 13/14 | MC-FA-E3 | 7 | 250 | E3 | P-204A |  |  | 0-100 | % LEL | instrument index
AT-0601 | FZ-06 | H2S detector | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 11 | FAR-100/FMC-FGS-1-A01 | TB09-21/22 | JB-FA-E4 | 1/2 | MC-FA-E4 | 1 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
AT-0602 | FZ-06 | H2S detector | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 12 | FAR-100/FMC-FGS-1-A01 | TB09-23/24 | JB-FA-E4 | 3/4 | MC-FA-E4 | 2 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
AT-0603 | FZ-06 | H2S detector | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI09 | 13 | FAR-100/FMC-FGS-1-A01 | TB09-25/26 | JB-FA-E4 | 5/6 | MC-FA-E4 | 3 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
AT-0604 | FZ-06 | H2S detector | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 1 | FAR-100/FMC-FGS-1-A01 | TB10-1/2 | JB-FA-E4 | 7/8 | MC-FA-E4 | 4 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0601 | FZ-06 | Flame detector (IR3) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 2 | FAR-100/FMC-FGS-1-A01 | TB10-3/4 | JB-FA-E4 | 9/10 | MC-FA-E4 | 5 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0602 | FZ-06 | Flame detector (IR3) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 3 | FAR-100/FMC-FGS-1-A01 | TB10-5/6 | JB-FA-E4 | 11/12 | MC-FA-E4 | 6 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
BD-0603 | FZ-06 | Flame detector (IR3) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 4 | FAR-100/FMC-FGS-1-A02 | TB10-7/8 | JB-FA-E4 | 13/14 | MC-FA-E4 | 7 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0601 | FZ-06 | Flammable gas detector (IR point) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 5 | FAR-100/FMC-FGS-1-A02 | TB10-9/10 | JB-FA-E4 | 15/16 | MC-FA-E4 | 8 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0602 | FZ-06 | Flammable gas detector (IR point) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 6 | FAR-100/FMC-FGS-1-A02 | TB10-11/12 | JB-FA-E4 | 17/18 | MC-FA-E4 | 9 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0603 | FZ-06 | Flammable gas detector (IR point) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 7 | FAR-100/FMC-FGS-1-A02 | TB10-13/14 | JB-FA-E4 | 19/20 | MC-FA-E4 | 10 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0604 | FZ-06 | Flammable gas detector (IR point) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 8 | FAR-100/FMC-FGS-1-A02 | TB10-15/16 | JB-FA-E4 | 21/22 | MC-FA-E4 | 11 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0605 | FZ-06 | Flammable gas detector (IR point) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 9 | FAR-100/FMC-FGS-1-A02 | TB10-17/18 | JB-FA-E4 | 23/24 | MC-FA-E4 | 12 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0606 | FZ-06 | Flammable gas detector (IR point) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 10 | FAR-100/FMC-FGS-1-A02 | TB10-19/20 | JB-FA-E4 | 25/26 | MC-FA-E4 | 13 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0607 | FZ-06 | Flammable gas detector (IR point) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 11 | FAR-100/FMC-FGS-1-A02 | TB10-21/22 | JB-FA-E4 | 27/28 | MC-FA-E4 | 14 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-0608 | FZ-06 | Flammable gas detector (IR point) | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 12 | FAR-100/FMC-FGS-1-A02 | TB10-23/24 | JB-FA-E4 | 29/30 | MC-FA-E4 | 15 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
GD-2505 | GD-2505 | Gas detector | Flammable gas detector (IR point), pump row P-205A/B | GD-2505 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI10 | 13 | FAR-100/FMC-FGS-1-A02 | TB10-25/26 | JB-FA-E4 | 31/32 | MC-FA-E4 | 16 | 310 | E4 | P-205A |  |  | 0-100 | % LEL | instrument index
GD-2506 | GD-2506 | Gas detector | Flammable gas detector (IR point), pump row P-206A/B | GD-2506 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI11 | 1 | FAR-100/FMC-FGS-1-A02 | TB11-1/2 | JB-FA-E4 | 33/34 | MC-FA-E4 | 17 | 310 | E4 | P-206A |  |  | 0-100 | % LEL | instrument index
GD-2509 | GD-2509 | Gas detector | H2S toxic gas detector (electrochemical), D-201 (1) | GD-2509 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI11 | 2 | FAR-100/FMC-FGS-1-A02 | TB11-3/4 | JB-FA-E4 | 35/36 | MC-FA-E4 | 18 | 300 | E4 | D-201 |  |  | 0-50 | ppm H2S | instrument index
GD-2510 | GD-2510 | Gas detector | H2S toxic gas detector (electrochemical), D-201 (2) | GD-2510 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI11 | 3 | FAR-100/FMC-FGS-1-A02 | TB11-5/6 | JB-FA-E4 | 37/38 | MC-FA-E4 | 19 | 300 | E4 | D-201 |  |  | 0-50 | ppm H2S | instrument index
GD-2512 | GD-2512 | Gas detector | H2S toxic gas detector (electrochemical), P-205 | GD-2512 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI11 | 4 | FAR-100/FMC-FGS-1-A02 | TB11-7/8 | JB-FA-E4 | 39/40 | MC-FA-E4 | 20 | 310 | E4 | P-205A |  |  | 0-50 | ppm H2S | instrument index
GD-2511 | GD-2511 | Gas detector | H2S toxic gas detector (electrochemical), D-202 | GD-2511 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | AI | 4-20 mA, 3-wire (F&G) | FGS-1-AI11 | 5 | FAR-100/FMC-FGS-1-A02 | TB11-9/10 | JB-FA-F4 | 1/2 | MC-FA-F4 | 1 | 310 | F4 | D-202 |  |  | 0-50 | ppm H2S | instrument index
HS-0101 | FZ-01 | Manual call point | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 1 | FAR-100/FMC-FGS-1-D01 | TB01-1/2 | JB-FD-A2 | 1/2 | MC-FD-A2 | 1 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0102 | FZ-01 | Manual call point | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 2 | FAR-100/FMC-FGS-1-D01 | TB01-3/4 | JB-FD-A2 | 3/4 | MC-FD-A2 | 2 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0103 | FZ-01 | Manual call point | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 3 | FAR-100/FMC-FGS-1-D01 | TB01-5/6 | JB-FD-A2 | 5/6 | MC-FD-A2 | 3 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-1540 | HS-1540 | Hand switch | Manual call point (MCP), desalting area | HS-1540 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 4 | FAR-100/FMC-FGS-1-D01 | TB01-7/8 | JB-FD-A2 | 7/8 | MC-FD-A2 | 4 | 90 | A2 | D-101A |  |  |  |  | instrument index
HS-0201 | FZ-02 | Manual call point | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 5 | FAR-100/FMC-FGS-1-D01 | TB01-9/10 | JB-FD-A4 | 1/2 | MC-FD-A4 | 1 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0202 | FZ-02 | Manual call point | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 6 | FAR-100/FMC-FGS-1-D01 | TB01-11/12 | JB-FD-A4 | 3/4 | MC-FD-A4 | 2 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0203 | FZ-02 | Manual call point | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 7 | FAR-100/FMC-FGS-1-D01 | TB01-13/14 | JB-FD-A4 | 5/6 | MC-FD-A4 | 3 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-1541 | HS-1541 | Hand switch | Manual call point (MCP), preheat bank area | HS-1541 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 8 | FAR-100/FMC-FGS-1-D01 | TB01-15/16 | JB-FD-A4 | 7/8 | MC-FD-A4 | 4 | 170 | A4 | E-106A |  |  |  |  | instrument index
HS-0401 | FZ-04 | Manual call point | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 9 | FAR-100/FMC-FGS-1-D01 | TB01-17/18 | JB-FD-B4 | 1/2 | MC-FD-B4 | 1 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0402 | FZ-04 | Manual call point | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 10 | FAR-100/FMC-FGS-1-D01 | TB01-19/20 | JB-FD-B4 | 3/4 | MC-FD-B4 | 2 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0403 | FZ-04 | Manual call point | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 11 | FAR-100/FMC-FGS-1-D01 | TB01-21/22 | JB-FD-B4 | 5/6 | MC-FD-B4 | 3 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-1544 | HS-1544 | Hand switch | Manual call point (MCP), light ends area | HS-1544 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 12 | FAR-100/FMC-FGS-1-D01 | TB01-23/24 | JB-FD-B4 | 7/8 | MC-FD-B4 | 4 | 140 | B4 | C-105 |  |  |  |  | instrument index
HS-1543 | HS-1543 | Hand switch | Manual call point (MCP), H-101 area | HS-1543 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 13 | FAR-100/FMC-FGS-1-D01 | TB01-25/26 | JB-FD-C2 | 1/2 | MC-FD-C2 | 1 | 100 | C2 | H-101 |  |  |  |  | instrument index
ZSC-1290 | HV-1290 | Hand-actuated (remote) on/off valve | H-101 snuffing steam valve (remote open from CCR / F&G) - Closed limit switch | HV-1290 | CFU-100-PR-PID-005 | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 14 | FAR-100/FMC-FGS-1-D01 | TB01-27/28 | JB-FD-C2 | 5/6 | MC-FD-C2 | 3 | 100 | C2 | H-101 |  |  |  |  | instrument index
ZSO-1290 | HV-1290 | Hand-actuated (remote) on/off valve | H-101 snuffing steam valve (remote open from CCR / F&G) - Open limit switch | HV-1290 | CFU-100-PR-PID-005 | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 15 | FAR-100/FMC-FGS-1-D01 | TB01-29/30 | JB-FD-C2 | 7/8 | MC-FD-C2 | 4 | 100 | C2 | H-101 |  |  |  |  | instrument index
BY-1121 | BY-1121 | Burner / flame BY | Fire confirmation from F&G (P-112 area) | BY-1121 | CFU-100-PR-PID-006 | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 16 | FAR-100/FMC-FGS-1-D01 | TB01-31/32 | JB-FD-C3 | 1/2 | MC-FD-C3 | 1 | 150 | C3 | P-112A | SIF-204 | SIL 1 |  |  | instrument index
HS-1545 | HS-1545 | Hand switch | Manual call point (MCP), CDU pump row area | HS-1545 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 17 | FAR-100/FMC-FGS-1-D01 | TB01-33/34 | JB-FD-C3 | 3/4 | MC-FD-C3 | 2 | 150 | C3 | P-112A |  |  |  |  | instrument index
HS-0301 | FZ-03 | Manual call point | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 18 | FAR-100/FMC-FGS-1-D01 | TB01-35/36 | JB-FD-C4 | 1/2 | MC-FD-C4 | 1 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0302 | FZ-03 | Manual call point | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 19 | FAR-100/FMC-FGS-1-D01 | TB01-37/38 | JB-FD-C4 | 3/4 | MC-FD-C4 | 2 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0303 | FZ-03 | Manual call point | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 20 | FAR-100/FMC-FGS-1-D01 | TB01-39/40 | JB-FD-C4 | 5/6 | MC-FD-C4 | 3 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0304 | FZ-03 | Manual call point | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 21 | FAR-100/FMC-FGS-1-D01 | TB01-41/42 | JB-FD-C4 | 7/8 | MC-FD-C4 | 4 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-1542 | HS-1542 | Hand switch | Manual call point (MCP), C-101 / OH area | HS-1542 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 22 | FAR-100/FMC-FGS-1-D01 | TB01-43/44 | JB-FD-C4 | 9/10 | MC-FD-C4 | 5 | 170 | C4 | C-101 |  |  |  |  | instrument index
HS-9502 | HS-9502 | Hand switch | Manual call point (MCP), fuel gas KO area | HS-9502 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 23 | FAR-100/FMC-FGS-1-D01 | TB01-45/46 | JB-FD-D1 | 1/2 | MC-FD-D1 | 1 | 140 | D1 | D-103 |  |  |  |  | instrument index
HS-0501 | FZ-05 | Manual call point | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 24 | FAR-100/FMC-FGS-1-D01 | TB01-47/48 | JB-FD-D2 | 1/2 | MC-FD-D2 | 1 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0502 | FZ-05 | Manual call point | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 25 | FAR-100/FMC-FGS-1-D01 | TB01-49/50 | JB-FD-D2 | 3/4 | MC-FD-D2 | 2 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0503 | FZ-05 | Manual call point | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI01 | 26 | FAR-100/FMC-FGS-1-D01 | TB01-51/52 | JB-FD-D2 | 5/6 | MC-FD-D2 | 3 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0504 | FZ-05 | Manual call point | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 1 | FAR-100/FMC-FGS-1-D01 | TB02-1/2 | JB-FD-D2 | 7/8 | MC-FD-D2 | 4 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-9501 | HS-9501 | Hand switch | Manual call point (MCP), flare KO / utilities area | HS-9501 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 2 | FAR-100/FMC-FGS-1-D01 | TB02-3/4 | JB-FD-D5 | 1/2 | MC-FD-D5 | 1 | 260 | D5 | D-104 |  |  |  |  | instrument index
HS-2519 | HS-2519 | Hand switch | Manual call point (MCP), H-201 area | HS-2519 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 3 | FAR-100/FMC-FGS-1-D01 | TB02-5/6 | JB-FD-E2 | 1/2 | MC-FD-E2 | 1 | 190 | E2 | H-201 |  |  |  |  | instrument index
ZSC-2190 | HV-2190 | Hand-actuated (remote) on/off valve | H-201 snuffing steam valve (remote open from CCR / F&G) - Closed limit switch | HV-2190 | CFU-200-PR-PID-012 | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 4 | FAR-100/FMC-FGS-1-D01 | TB02-7/8 | JB-FD-E2 | 5/6 | MC-FD-E2 | 3 | 190 | E2 | H-201 |  |  |  |  | instrument index
ZSO-2190 | HV-2190 | Hand-actuated (remote) on/off valve | H-201 snuffing steam valve (remote open from CCR / F&G) - Open limit switch | HV-2190 | CFU-200-PR-PID-012 | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 5 | FAR-100/FMC-FGS-1-D01 | TB02-9/10 | JB-FD-E2 | 7/8 | MC-FD-E2 | 4 | 190 | E2 | H-201 |  |  |  |  | instrument index
BY-2041 | BY-2041 | Burner / flame BY | Fire confirmation from F&G (P-204 area) | BY-2041 | CFU-200-PR-PID-013 | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 6 | FAR-100/FMC-FGS-1-D01 | TB02-11/12 | JB-FD-E3 | 1/2 | MC-FD-E3 | 1 | 250 | E3 | P-204A | SIF-204 | SIL 1 |  |  | instrument index
HS-0601 | FZ-06 | Manual call point | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 7 | FAR-100/FMC-FGS-1-D01 | TB02-13/14 | JB-FD-E4 | 1/2 | MC-FD-E4 | 1 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0602 | FZ-06 | Manual call point | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 8 | FAR-100/FMC-FGS-1-D01 | TB02-15/16 | JB-FD-E4 | 3/4 | MC-FD-E4 | 2 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-0603 | FZ-06 | Manual call point | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 9 | FAR-100/FMC-FGS-1-D01 | TB02-17/18 | JB-FD-E4 | 5/6 | MC-FD-E4 | 3 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HS-2518 | HS-2518 | Hand switch | Manual call point (MCP), VDU area | HS-2518 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 10 | FAR-100/FMC-FGS-1-D01 | TB02-19/20 | JB-FD-E4 | 7/8 | MC-FD-E4 | 4 | 270 | E4 | C-201 |  |  |  |  | instrument index
HS-2520 | HS-2520 | Hand switch | Manual call point (MCP), ejector / hotwell area | HS-2520 | F&G LAYOUT (BY OTHERS) | F&G | FGS-1 | DI | 24 VDC dry contact / NAMUR | FGS-1-DI02 | 11 | FAR-100/FMC-FGS-1-D01 | TB02-21/22 | JB-FD-E4 | 9/10 | MC-FD-E4 | 5 | 300 | E4 | D-201 |  |  |  |  | instrument index
XL-0101 | FZ-01 | Beacon / sounder | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 1 | FAR-100/FMC-FGS-1-D01 | TB01-1/2 | JB-FD-A2 | 9/10 | MC-FD-A2 | 5 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0102 | FZ-01 | Beacon / sounder | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 2 | FAR-100/FMC-FGS-1-D01 | TB01-3/4 | JB-FD-A2 | 11/12 | MC-FD-A2 | 6 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0103 | FZ-01 | Beacon / sounder | Desalting & crude charge (FZ-01) | FZ-01 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 3 | FAR-100/FMC-FGS-1-D01 | TB01-5/6 | JB-FD-A2 | 13/14 | MC-FD-A2 | 7 | 100 | A2 | FZ-01 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0201 | FZ-02 | Beacon / sounder | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 4 | FAR-100/FMC-FGS-1-D01 | TB01-7/8 | JB-FD-A4 | 9/10 | MC-FD-A4 | 5 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0202 | FZ-02 | Beacon / sounder | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 5 | FAR-100/FMC-FGS-1-D01 | TB01-9/10 | JB-FD-A4 | 11/12 | MC-FD-A4 | 6 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0203 | FZ-02 | Beacon / sounder | Preheat exchanger bank (FZ-02) | FZ-02 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 6 | FAR-100/FMC-FGS-1-D01 | TB01-11/12 | JB-FD-A4 | 13/14 | MC-FD-A4 | 7 | 160 | A4 | FZ-02 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0401 | FZ-04 | Beacon / sounder | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 7 | FAR-100/FMC-FGS-1-D01 | TB01-13/14 | JB-FD-B4 | 9/10 | MC-FD-B4 | 5 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0402 | FZ-04 | Beacon / sounder | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 8 | FAR-100/FMC-FGS-1-D01 | TB01-15/16 | JB-FD-B4 | 11/12 | MC-FD-B4 | 6 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0403 | FZ-04 | Beacon / sounder | Light ends C-105/C-106 & LPG pumps (FZ-04) | FZ-04 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 9 | FAR-100/FMC-FGS-1-D01 | TB01-17/18 | JB-FD-B4 | 13/14 | MC-FD-B4 | 7 | 120 | B4 | FZ-04 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HV-1290 | HV-1290 | Hand-actuated (remote) on/off valve | H-101 snuffing steam valve (remote open from CCR / F&G) - SOV de-energise to trip | HV-1290 | CFU-100-PR-PID-005 | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 10 | FAR-100/FMC-FGS-1-D01 | TB01-19/20 | JB-FD-C2 | 3/4 | MC-FD-C2 | 2 | 100 | C2 | H-101 |  |  |  |  | instrument index
XL-0301 | FZ-03 | Beacon / sounder | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 11 | FAR-100/FMC-FGS-1-D01 | TB01-21/22 | JB-FD-C4 | 11/12 | MC-FD-C4 | 6 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0302 | FZ-03 | Beacon / sounder | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 12 | FAR-100/FMC-FGS-1-D01 | TB01-23/24 | JB-FD-C4 | 13/14 | MC-FD-C4 | 7 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0303 | FZ-03 | Beacon / sounder | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO01 | 13 | FAR-100/FMC-FGS-1-D01 | TB01-25/26 | JB-FD-C4 | 15/16 | MC-FD-C4 | 8 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0304 | FZ-03 | Beacon / sounder | C-101 / strippers / OH system & pumps (FZ-03) | FZ-03 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO02 | 1 | FAR-100/FMC-FGS-1-D01 | TB02-1/2 | JB-FD-C4 | 17/18 | MC-FD-C4 | 9 | 170 | C4 | FZ-03 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0501 | FZ-05 | Beacon / sounder | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO02 | 2 | FAR-100/FMC-FGS-1-D01 | TB02-3/4 | JB-FD-D2 | 9/10 | MC-FD-D2 | 5 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0502 | FZ-05 | Beacon / sounder | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO02 | 3 | FAR-100/FMC-FGS-1-D01 | TB02-5/6 | JB-FD-D2 | 11/12 | MC-FD-D2 | 6 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0503 | FZ-05 | Beacon / sounder | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO02 | 4 | FAR-100/FMC-FGS-1-D01 | TB02-7/8 | JB-FD-D2 | 13/14 | MC-FD-D2 | 7 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0504 | FZ-05 | Beacon / sounder | Fired heaters H-101/H-201 & FG KO (FZ-05) | FZ-05 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO02 | 5 | FAR-100/FMC-FGS-1-D01 | TB02-9/10 | JB-FD-D2 | 15/16 | MC-FD-D2 | 8 | 140 | D2 | FZ-05 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
HV-2190 | HV-2190 | Hand-actuated (remote) on/off valve | H-201 snuffing steam valve (remote open from CCR / F&G) - SOV de-energise to trip | HV-2190 | CFU-200-PR-PID-012 | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO02 | 6 | FAR-100/FMC-FGS-1-D01 | TB02-11/12 | JB-FD-E2 | 3/4 | MC-FD-E2 | 2 | 190 | E2 | H-201 |  |  |  |  | instrument index
XL-0601 | FZ-06 | Beacon / sounder | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO02 | 7 | FAR-100/FMC-FGS-1-D01 | TB02-13/14 | JB-FD-E4 | 11/12 | MC-FD-E4 | 6 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0602 | FZ-06 | Beacon / sounder | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO02 | 8 | FAR-100/FMC-FGS-1-D01 | TB02-15/16 | JB-FD-E4 | 13/14 | MC-FD-E4 | 7 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)
XL-0603 | FZ-06 | Beacon / sounder | VDU C-201, ejectors & hotwell (FZ-06) | FZ-06 |  | F&G | FGS-1 | DO | 24 VDC interposing relay | FGS-1-DO02 | 9 | FAR-100/FMC-FGS-1-D01 | TB02-17/18 | JB-FD-E4 | 15/16 | MC-FD-E4 | 8 | 280 | E4 | FZ-06 |  | SIL 2 (F&G) |  |  | F&G allowance (mapping study)

## Basis
I/O list CFU-000-IC-IOL-001 (xlsx) and data/io_list.json, derived from data/instruments.json.
Rules (FEED):
* every instrument with a field signal becomes one or more I/O points (AI/AO/DI/DO);
'Local' instruments and soft function blocks have no physical I/O;
* shutdown valves (DO SOV + 2 DI) expand to XV (DO), ZSO (DI), ZSC (DI);
* BMS = heater burner-management functions (SIF-101..106, SIF-201/202, flame scanners) - hosted in the
SIS logic solver hardware but configured as a separate application;
* motor interfaces (run / available DI, start / stop DO) are derived from equipment.json drivers;
* F&G field devices are a FEED allowance per fire zone (detector mapping study to follow);
* I&C additions from the control philosophy (analysers, FG flow, ambient T) are flagged 'I&C addition';
* DCS controller allocation by P&ID sheet / area; SIS split CDU / VDU;
* installed spare: each I/O card filled to <= ~80 % (AI 13/16, AO 6/8, DI 26/32, DO 13/16) -> >= 20 % spare.
Junction boxes are zoned on a 40 m x 30 m grid of the plot (data/layout.json); one JB per system per zone
(split at 24 pairs); multicores run to the marshalling cabinets in FAR-100.