## Cable Schedule
100 kBPSD Crude & Vacuum Distillation Unit - Power Cable Schedule
CFU-000-EL-CBL-001 Rev A (Issued for review (FEED)), 2026-10-02 ¦ Generic Refinery - Gulf Coast
No. | Cable tag | From | To | Service | kV | Design I (A) | Length (m) | Length basis | Cable (cores x size, type) | Size mm2 | Runs | Ampacity derated (A) | VD running % | VD start (cable) % | Bus dip at start % | Terminal dip % | SC min mm2 | Protective device | CT | Relays (ANSI) | Notes
1 | CBL-INC-A | Refinery main substation (OSBL) | SWG-101A incomer | 13.8 kV incomer | 13.8 | 392.2 | 600 | assumed | 1 x (3 x 1C x 240 mm2) Cu/XLPE/CWS/PVC 8.7/15 kV, trefoil | 240 | 1 | 444.1 | 0.42 |  |  |  | 155.8 | VCB 1200 A (both ends) |  |  | Length assumed (OSBL route TBC); sized for full unit load on one incomer (ONAF rating of one transformer)
2 | CBL-TR-101-P | SWG-101A | TR-101 primary | Transformer feeder | 13.8 | 392.2 | 30 | SS-100 yard | 1 x (3 x 1C x 240 mm2) Cu/XLPE/CWS/PVC 8.7/15 kV, trefoil | 240 | 1 | 444.1 | 0.02 |  |  |  | 159.3 | VCB 1200 A
3 | CBL-TR-101-S | TR-101 secondary | SWG-102A incomer | Transformer secondary | 4.16 | 1301.1 | 25 | SS-100 yard | 2 x (3 x 1C x 500 mm2) Cu/XLPE/CWS/PVC 3.6/6 kV, trefoil | 500 | 2 | 1310.4 | 0.07 |  |  |  | 78.6 | VCB 2000 A |  |  | Alternative: 5 kV cable bus / non-segregated bus duct
4 | CBL-TR-103-P | SWG-102A | TR-103 primary | Transformer feeder | 4.16 | 520.4 | 30 | SS-100 yard | 2 x 3C x 150 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 150 | 2 | 589.7 | 0.06 |  |  |  | 78.6 | VCB 1200 A
5 | BD-TR-103-S | TR-103 secondary | MCC-101A incomer | Transformer secondary | 0.48 | 4510.5 | 15 | SS-100 yard | Non-segregated phase bus duct 5000 A, Cu, 65 kA |  | 1 | 5000 | 0.1 |  |  |  |  | ACB 5000 A
6 | CBL-INC-B | Refinery main substation (OSBL) | SWG-101B incomer | 13.8 kV incomer | 13.8 | 392.2 | 600 | assumed | 1 x (3 x 1C x 240 mm2) Cu/XLPE/CWS/PVC 8.7/15 kV, trefoil | 240 | 1 | 444.1 | 0.42 |  |  |  | 155.8 | VCB 1200 A (both ends) |  |  | Length assumed (OSBL route TBC); sized for full unit load on one incomer (ONAF rating of one transformer)
7 | CBL-TR-102-P | SWG-101B | TR-102 primary | Transformer feeder | 13.8 | 392.2 | 30 | SS-100 yard | 1 x (3 x 1C x 240 mm2) Cu/XLPE/CWS/PVC 8.7/15 kV, trefoil | 240 | 1 | 444.1 | 0.02 |  |  |  | 159.3 | VCB 1200 A
8 | CBL-TR-102-S | TR-102 secondary | SWG-102B incomer | Transformer secondary | 4.16 | 1301.1 | 25 | SS-100 yard | 2 x (3 x 1C x 500 mm2) Cu/XLPE/CWS/PVC 3.6/6 kV, trefoil | 500 | 2 | 1310.4 | 0.07 |  |  |  | 78.6 | VCB 2000 A |  |  | Alternative: 5 kV cable bus / non-segregated bus duct
9 | CBL-TR-104-P | SWG-102B | TR-104 primary | Transformer feeder | 4.16 | 520.4 | 30 | SS-100 yard | 2 x 3C x 150 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 150 | 2 | 589.7 | 0.06 |  |  |  | 78.6 | VCB 1200 A
10 | BD-TR-104-S | TR-104 secondary | MCC-101B incomer | Transformer secondary | 0.48 | 4510.5 | 15 | SS-100 yard | Non-segregated phase bus duct 5000 A, Cu, 65 kA |  | 1 | 5000 | 0.1 |  |  |  |  | ACB 5000 A
11 | CBL-P-101A | SWG-102A | P-101A | Crude charge pump A | 4.16 | 114.7 | 100 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.17 | 0.55 | 5.33 | 5.88 | 55.6 | VCB 1200 A, DOL | 150/5 A | 50/51, 50G, 46, 49, 87M, 27, 66, 86
12 | CBL-P-101B | SWG-102B | P-101B | Crude charge pump B | 4.16 | 114.7 | 95 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.16 | 0.52 | 5.32 | 5.84 | 55.6 | VCB 1200 A, DOL | 150/5 A | 50/51, 50G, 46, 49, 87M, 27, 66, 86
13 | CBL-P-102A | SWG-102A | P-102A | Desalted crude booster pump A | 4.16 | 114.7 | 90 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.15 | 0.49 | 5.32 | 5.81 | 55.6 | VCB 1200 A, DOL | 150/5 A | 50/51, 50G, 46, 49, 87M, 27, 66, 86
14 | CBL-P-102B | SWG-102B | P-102B | Desalted crude booster pump B | 4.16 | 114.7 | 95 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.16 | 0.52 | 5.33 | 5.85 | 55.6 | VCB 1200 A, DOL | 150/5 A | 50/51, 50G, 46, 49, 87M, 27, 66, 86
15 | CBL-P-112A | SWG-102A | P-112A | Atm. residue / vacuum heater charge pump A | 4.16 | 52.6 | 155 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.12 | 0.39 | 2.51 | 2.9 | 55.6 | VCB 1200 A, DOL | 75/5 A | 50/51, 50G, 46, 49, 27, 66, 86
16 | CBL-P-112B | SWG-102B | P-112B | Atm. residue / vacuum heater charge pump B | 4.16 | 52.6 | 160 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.12 | 0.4 | 2.51 | 2.92 | 55.6 | VCB 1200 A, DOL | 75/5 A | 50/51, 50G, 46, 49, 27, 66, 86
17 | CBL-P-202A | SWG-102A | P-202A | HVGO pumparound / product pump A | 4.16 | 33.4 | 250 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.12 | 0.4 | 1.61 | 2.01 | 55.6 | VCB 1200 A, DOL | 50/5 A | 50/51, 50G, 46, 49, 27, 66, 86
18 | CBL-P-202B | SWG-102B | P-202B | HVGO pumparound / product pump B | 4.16 | 33.4 | 250 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.12 | 0.4 | 1.61 | 2.01 | 55.6 | VCB 1200 A, DOL | 50/5 A | 50/51, 50G, 46, 49, 27, 66, 86
19 | CBL-K-102A | VFD-K-102A | K-102A | H-101 induced-draft fan A | 4.16 | 33.4 | 110 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.05 |  |  |  | 55.6 | VCB 1200 A + VFD-K-102A (MV drive, 18-pulse/AFE) | 50/5 A | 50/51, 50N/51N, 27, 86 (motor protection in VFD: 49, 46, 37)
20 | CBL-K-102B | VFD-K-102B | K-102B | H-101 induced-draft fan B | 4.16 | 33.4 | 115 | layout | 3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 70 | 1 | 185.6 | 0.06 |  |  |  | 55.6 | VCB 1200 A + VFD-K-102B (MV drive, 18-pulse/AFE) | 50/5 A | 50/51, 50N/51N, 27, 86 (motor protection in VFD: 49, 46, 37)
21 | CBL-P-103A | MCC-101A | P-103A | Atm. reflux pump A | 0.48 | 82.3 | 135 | layout | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 2.49 | 8.19 | 1.25 | 9.44 | 8.6 | MCCB 150 A (250 AF) + DOL, NEMA size 4
22 | CBL-P-103B | MCC-101B | P-103B | Atm. reflux pump B | 0.48 | 82.3 | 140 | layout | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 2.58 | 8.49 | 1.25 | 9.75 | 8.6 | MCCB 150 A (250 AF) + DOL, NEMA size 4
23 | CBL-P-104A | MCC-101A | P-104A | Unstabilised naphtha pump A | 0.48 | 232.8 | 140 | layout | 3C x 185 + E95 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 185 | 1 | 332 | 1.75 | 8.98 | 3.47 | 12.45 | 17.1 | MCCB 450 A (600 AF) + DOL, NEMA size 6
24 | CBL-P-104B | MCC-101B | P-104B | Unstabilised naphtha pump B | 0.48 | 232.8 | 145 | layout | 3C x 185 + E95 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 185 | 1 | 332 | 1.81 | 9.3 | 3.47 | 12.77 | 17.1 | MCCB 450 A (600 AF) + DOL, NEMA size 6
25 | CBL-P-105A | MCC-101A | P-105A | Overhead sour water pump A | 0.48 | 9.2 | 150 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 2.44 | 6.96 | 0.14 | 7.1 | 1.6 | MCCB 20 A (125 AF) + DOL, NEMA size 0
26 | CBL-P-105B | MCC-101B | P-105B | Overhead sour water pump B | 0.48 | 9.2 | 150 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 2.44 | 6.96 | 0.14 | 7.1 | 1.6 | MCCB 20 A (125 AF) + DOL, NEMA size 0
27 | CBL-P-106A | MCC-101A | P-106A | TPA pumparound pump A | 0.48 | 160.1 | 190 | layout | 3C x 95 + E50 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 95 | 1 | 216.9 | 2.78 | 11.38 | 2.41 | 13.79 | 12.1 | MCCB 300 A (400 AF) + DOL, NEMA size 5
28 | CBL-P-106B | MCC-101B | P-106B | TPA pumparound pump B | 0.48 | 160.1 | 190 | layout | 3C x 95 + E50 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 95 | 1 | 216.9 | 2.78 | 11.38 | 2.41 | 13.79 | 12.1 | MCCB 300 A (400 AF) + DOL, NEMA size 5
29 | CBL-P-107A | MCC-101A | P-107A | MPA pumparound pump A | 0.48 | 232.8 | 195 | layout | 3C x 240 + E120 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 240 | 1 | 391.7 | 2.01 | 11.38 | 3.47 | 14.85 | 17.1 | MCCB 450 A (600 AF) + DOL, NEMA size 6
30 | CBL-P-107B | MCC-101B | P-107B | MPA pumparound pump B | 0.48 | 232.8 | 195 | layout | 3C x 240 + E120 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 240 | 1 | 391.7 | 2.01 | 11.38 | 3.47 | 14.85 | 17.1 | MCCB 450 A (600 AF) + DOL, NEMA size 6
31 | CBL-P-108A | MCC-101A | P-108A | BPA pumparound pump A | 0.48 | 192.1 | 160 | layout | 3C x 120 + E70 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 120 | 1 | 251.9 | 2.32 | 10.21 | 2.88 | 13.09 | 12.1 | MCCB 350 A (400 AF) + DOL, NEMA size 5
32 | CBL-P-108B | MCC-101B | P-108B | BPA pumparound pump B | 0.48 | 192.1 | 165 | layout | 3C x 120 + E70 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 120 | 1 | 251.9 | 2.39 | 10.53 | 2.88 | 13.41 | 12.1 | MCCB 350 A (400 AF) + DOL, NEMA size 5
33 | CBL-P-109A | MCC-101A | P-109A | Kero product pump A | 0.48 | 82.3 | 170 | layout | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 3.13 | 10.31 | 1.25 | 11.57 | 8.6 | MCCB 150 A (250 AF) + DOL, NEMA size 4
34 | CBL-P-109B | MCC-101B | P-109B | Kero product pump B | 0.48 | 82.3 | 170 | layout | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 3.13 | 10.31 | 1.25 | 11.57 | 8.6 | MCCB 150 A (250 AF) + DOL, NEMA size 4
35 | CBL-P-110A | MCC-101A | P-110A | Diesel product pump A | 0.48 | 112.2 | 175 | layout | 3C x 70 + E35 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 70 | 1 | 179.1 | 2.37 | 8.89 | 1.7 | 10.59 | 8.6 | MCCB 200 A (250 AF) + DOL, NEMA size 5
36 | CBL-P-110B | MCC-101B | P-110B | Diesel product pump B | 0.48 | 112.2 | 180 | layout | 3C x 70 + E35 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 70 | 1 | 179.1 | 2.44 | 9.15 | 1.7 | 10.85 | 8.6 | MCCB 200 A (250 AF) + DOL, NEMA size 5
37 | CBL-P-111A | MCC-101A | P-111A | Ago product pump A | 0.48 | 67.3 | 180 | layout | 3C x 25 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 25 | 1 | 92.5 | 3.69 | 11.52 | 1.03 | 12.55 | 4.9 | MCCB 125 A (125 AF) + DOL, NEMA size 4
38 | CBL-P-111B | MCC-101B | P-111B | Ago product pump B | 0.48 | 67.3 | 185 | layout | 3C x 25 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 25 | 1 | 92.5 | 3.79 | 11.84 | 1.03 | 12.87 | 4.9 | MCCB 125 A (125 AF) + DOL, NEMA size 4
39 | CBL-P-114A | MCC-101A | P-114A | Desalter wash water pump A | 0.48 | 46.7 | 70 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 1.53 | 4.56 | 0.71 | 5.27 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
40 | CBL-P-114B | MCC-101B | P-114B | Desalter wash water pump B | 0.48 | 46.7 | 75 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 1.64 | 4.88 | 0.71 | 5.6 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
41 | CBL-P-115A | MCC-101A | P-115A | Stabiliser reflux / LPG pump A | 0.48 | 28.8 | 125 | layout | 3C x 6 + E6 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 6 | 1 | 39.3 | 4.41 | 12.31 | 0.44 | 12.75 | 2.7 | MCCB 60 A (125 AF) + DOL, NEMA size 2
42 | CBL-P-115B | MCC-101B | P-115B | Stabiliser reflux / LPG pump B | 0.48 | 28.8 | 130 | layout | 3C x 6 + E6 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 6 | 1 | 39.3 | 4.58 | 12.8 | 0.44 | 13.24 | 2.7 | MCCB 60 A (125 AF) + DOL, NEMA size 2
43 | CBL-P-116A | MCC-101A | P-116A | Splitter reflux / LN pump A | 0.48 | 82.3 | 115 | layout | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 2.12 | 6.98 | 1.25 | 8.23 | 8.6 | MCCB 150 A (250 AF) + DOL, NEMA size 4
44 | CBL-P-116B | MCC-101B | P-116B | Splitter reflux / LN pump B | 0.48 | 82.3 | 115 | layout | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 2.12 | 6.98 | 1.25 | 8.23 | 8.6 | MCCB 150 A (250 AF) + DOL, NEMA size 4
45 | CBL-P-117A | MCC-101A | P-117A | Heavy naphtha product pump A | 0.48 | 67.3 | 120 | layout | 3C x 25 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 25 | 1 | 92.5 | 2.46 | 7.68 | 1.03 | 8.71 | 4.9 | MCCB 125 A (125 AF) + DOL, NEMA size 4
46 | CBL-P-117B | MCC-101B | P-117B | Heavy naphtha product pump B | 0.48 | 67.3 | 125 | layout | 3C x 25 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 25 | 1 | 92.5 | 2.56 | 8 | 1.03 | 9.03 | 4.9 | MCCB 125 A (125 AF) + DOL, NEMA size 4
47 | CBL-P-118 | MCC-101B | P-118 | Desalter mud-wash / recycle (single, intermittent) | 0.48 | 12.6 | 75 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 1.66 | 4.74 | 0.19 | 4.94 | 1.6 | MCCB 25 A (125 AF) + DOL, NEMA size 1
48 | CBL-P-119A | MCC-101A | P-119A | Flare KO drum pump-out pump A | 0.48 | 12.6 | 235 | layout | 3C x 6 + E6 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 6 | 1 | 39.3 | 3.5 | 10.11 | 0.19 | 10.31 | 1.6 | MCCB 25 A (125 AF) + DOL, NEMA size 1
49 | CBL-P-119B | MCC-101B | P-119B | Flare KO drum pump-out pump B | 0.48 | 12.6 | 235 | layout | 3C x 6 + E6 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 6 | 1 | 39.3 | 3.5 | 10.11 | 0.19 | 10.31 | 1.6 | MCCB 25 A (125 AF) + DOL, NEMA size 1
50 | CBL-P-201A | MCC-101A | P-201A | LVGO pumparound / product pump A | 0.48 | 160.1 | 255 | layout | 3C x 150 + E95 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 150 | 1 | 290.5 | 2.6 | 12.31 | 2.41 | 14.73 | 12.1 | MCCB 300 A (400 AF) + DOL, NEMA size 5
51 | CBL-P-201B | MCC-101B | P-201B | LVGO pumparound / product pump B | 0.48 | 160.1 | 260 | layout | 3C x 150 + E95 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 150 | 1 | 290.5 | 2.65 | 12.56 | 2.41 | 14.97 | 12.1 | MCCB 300 A (400 AF) + DOL, NEMA size 5
52 | CBL-P-203A | MCC-101A | P-203A | Slop wax pump A | 0.48 | 9.2 | 240 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 3.9 | 11.13 | 0.14 | 11.27 | 1.6 | MCCB 20 A (125 AF) + DOL, NEMA size 0
53 | CBL-P-203B | MCC-101B | P-203B | Slop wax pump B | 0.48 | 9.2 | 245 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 3.98 | 11.36 | 0.14 | 11.51 | 1.6 | MCCB 20 A (125 AF) + DOL, NEMA size 0
54 | CBL-P-204A | MCC-101A | P-204A | Vacuum residue (incl. quench) pump A | 0.48 | 192.1 | 235 | layout | 3C x 240 + E120 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 240 | 1 | 391.7 | 1.99 | 11.31 | 2.88 | 14.19 | 12.1 | MCCB 350 A (400 AF) + DOL, NEMA size 5
55 | CBL-P-204B | MCC-101B | P-204B | Vacuum residue (incl. quench) pump B | 0.48 | 192.1 | 240 | layout | 3C x 240 + E120 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 240 | 1 | 391.7 | 2.04 | 11.55 | 2.88 | 14.43 | 12.1 | MCCB 350 A (400 AF) + DOL, NEMA size 5
56 | CBL-P-205A | MCC-101A | P-205A | Hotwell sour water pump A | 0.48 | 6.2 | 285 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 3.12 | 8.89 | 0.1 | 8.99 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
57 | CBL-P-205B | MCC-101B | P-205B | Hotwell sour water pump B | 0.48 | 6.2 | 285 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 3.12 | 8.89 | 0.1 | 8.99 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
58 | CBL-P-206A | MCC-101A | P-206A | Hotwell slop oil pump A | 0.48 | 1.5 | 290 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.7 | 2.16 | 0.02 | 2.19 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
59 | CBL-P-206B | MCC-101B | P-206B | Hotwell slop oil pump B | 0.48 | 1.5 | 295 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.72 | 2.2 | 0.02 | 2.22 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
60 | CBL-K-101A | MCC-101A | K-101A | H-101 forced-draft fan A | 0.48 | 134.6 | 100 | layout | 3C x 70 + E35 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 70 | 1 | 179.1 | 1.63 | 6.1 | 2.04 | 8.13 | 8.6 | MCCB 250 A (250 AF) + DOL, NEMA size 5
61 | CBL-K-101B | MCC-101B | K-101B | H-101 forced-draft fan B | 0.48 | 134.6 | 105 | layout | 3C x 70 + E35 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 70 | 1 | 179.1 | 1.71 | 6.4 | 2.04 | 8.44 | 8.6 | MCCB 250 A (250 AF) + DOL, NEMA size 5
62 | CBL-A-101-M1 | VFD-A-101-M1 | A-101-M1 | Atm. overhead condenser - fan motor 1/6 (VFD) | 0.48 | 82.3 | 140 | layout | 3C x 35 + 3E x 11.6667 mm2 Cu/XLPE/CWS/SWA/PVC 0.6/1 kV, symmetrical VFD cable | 35 | 1 | 115 | 2.58 |  |  |  | 4.9 | MCCB 100 A (125 AF) + VFD (6-pulse + harmonic filter)
63 | CBL-A-101-M2 | VFD-A-101-M2 | A-101-M2 | Atm. overhead condenser - fan motor 2/6 (VFD) | 0.48 | 82.3 | 140 | layout | 3C x 35 + 3E x 11.6667 mm2 Cu/XLPE/CWS/SWA/PVC 0.6/1 kV, symmetrical VFD cable | 35 | 1 | 115 | 2.58 |  |  |  | 4.9 | MCCB 100 A (125 AF) + VFD (6-pulse + harmonic filter)
64 | CBL-A-101-M3 | VFD-A-101-M3 | A-101-M3 | Atm. overhead condenser - fan motor 3/6 (VFD) | 0.48 | 82.3 | 145 | layout | 3C x 35 + 3E x 11.6667 mm2 Cu/XLPE/CWS/SWA/PVC 0.6/1 kV, symmetrical VFD cable | 35 | 1 | 115 | 2.67 |  |  |  | 4.9 | MCCB 100 A (125 AF) + VFD (6-pulse + harmonic filter)
65 | CBL-A-101-M4 | VFD-A-101-M4 | A-101-M4 | Atm. overhead condenser - fan motor 4/6 (VFD) | 0.48 | 82.3 | 145 | layout | 3C x 35 + 3E x 11.6667 mm2 Cu/XLPE/CWS/SWA/PVC 0.6/1 kV, symmetrical VFD cable | 35 | 1 | 115 | 2.67 |  |  |  | 4.9 | MCCB 100 A (125 AF) + VFD (6-pulse + harmonic filter)
66 | CBL-A-101-M5 | VFD-A-101-M5 | A-101-M5 | Atm. overhead condenser - fan motor 5/6 (VFD) | 0.48 | 82.3 | 150 | layout | 3C x 35 + 3E x 11.6667 mm2 Cu/XLPE/CWS/SWA/PVC 0.6/1 kV, symmetrical VFD cable | 35 | 1 | 115 | 2.76 |  |  |  | 4.9 | MCCB 100 A (125 AF) + VFD (6-pulse + harmonic filter)
67 | CBL-A-101-M6 | VFD-A-101-M6 | A-101-M6 | Atm. overhead condenser - fan motor 6/6 (VFD) | 0.48 | 82.3 | 150 | layout | 3C x 35 + 3E x 11.6667 mm2 Cu/XLPE/CWS/SWA/PVC 0.6/1 kV, symmetrical VFD cable | 35 | 1 | 115 | 2.76 |  |  |  | 4.9 | MCCB 100 A (125 AF) + VFD (6-pulse + harmonic filter)
68 | CBL-A-103-M1 | MCC-101A | A-103-M1 | Kero cooler - fan motor 1/2 | 0.48 | 17.1 | 175 | layout | 3C x 6 + E6 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 6 | 1 | 39.3 | 3.67 | 10.25 | 0.26 | 10.51 | 1.6 | MCCB 30 A (125 AF) + DOL, NEMA size 1
69 | CBL-A-103-M2 | MCC-101B | A-103-M2 | Kero cooler - fan motor 2/2 | 0.48 | 17.1 | 175 | layout | 3C x 6 + E6 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 6 | 1 | 39.3 | 3.67 | 10.25 | 0.26 | 10.51 | 1.6 | MCCB 30 A (125 AF) + DOL, NEMA size 1
70 | CBL-A-104-M1 | MCC-101A | A-104-M1 | Diesel cooler - fan motor 1/2 | 0.48 | 28.8 | 180 | layout | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 3.8 | 10.92 | 0.44 | 11.37 | 2.7 | MCCB 60 A (125 AF) + DOL, NEMA size 2
71 | CBL-A-104-M2 | MCC-101B | A-104-M2 | Diesel cooler - fan motor 2/2 | 0.48 | 28.8 | 180 | layout | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 3.8 | 10.92 | 0.44 | 11.37 | 2.7 | MCCB 60 A (125 AF) + DOL, NEMA size 2
72 | CBL-A-105-M1 | MCC-101A | A-105-M1 | Ago cooler - fan motor 1/2 | 0.48 | 46.7 | 190 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 4.15 | 12.37 | 0.71 | 13.08 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
73 | CBL-A-105-M2 | MCC-101B | A-105-M2 | Ago cooler - fan motor 2/2 | 0.48 | 46.7 | 190 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 4.15 | 12.37 | 0.71 | 13.08 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
74 | CBL-A-106-M1 | MCC-101A | A-106-M1 | Stabiliser overhead condenser - fan motor 1/2 | 0.48 | 17.1 | 120 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 3.75 | 10.33 | 0.26 | 10.59 | 1.6 | MCCB 30 A (125 AF) + DOL, NEMA size 1
75 | CBL-A-106-M2 | MCC-101B | A-106-M2 | Stabiliser overhead condenser - fan motor 2/2 | 0.48 | 17.1 | 120 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 3.75 | 10.33 | 0.26 | 10.59 | 1.6 | MCCB 30 A (125 AF) + DOL, NEMA size 1
76 | CBL-A-107-M1 | MCC-101A | A-107-M1 | Splitter overhead condenser - fan motor 1/4 | 0.48 | 46.7 | 110 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 2.4 | 7.16 | 0.71 | 7.87 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
77 | CBL-A-107-M2 | MCC-101B | A-107-M2 | Splitter overhead condenser - fan motor 2/4 | 0.48 | 46.7 | 110 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 2.4 | 7.16 | 0.71 | 7.87 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
78 | CBL-A-107-M3 | MCC-101A | A-107-M3 | Splitter overhead condenser - fan motor 3/4 | 0.48 | 46.7 | 115 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 2.51 | 7.48 | 0.71 | 8.2 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
79 | CBL-A-107-M4 | MCC-101B | A-107-M4 | Splitter overhead condenser - fan motor 4/4 | 0.48 | 46.7 | 115 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 2.51 | 7.48 | 0.71 | 8.2 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
80 | CBL-A-108-M1 | MCC-101A | A-108-M1 | Heavy naphtha product cooler - fan motor 1/2 | 0.48 | 46.7 | 130 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 2.84 | 8.46 | 0.71 | 9.18 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
81 | CBL-A-108-M2 | MCC-101B | A-108-M2 | Heavy naphtha product cooler - fan motor 2/2 | 0.48 | 46.7 | 130 | layout | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 2.84 | 8.46 | 0.71 | 9.18 | 4.9 | MCCB 90 A (125 AF) + DOL, NEMA size 3
82 | CBL-A-201-M1 | MCC-101A | A-201-M1 | Lvgo cooler - fan motor 1/2 | 0.48 | 23.3 | 225 | layout | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 3.86 | 11.07 | 0.36 | 11.43 | 2.7 | MCCB 45 A (125 AF) + DOL, NEMA size 2
83 | CBL-A-201-M2 | MCC-101B | A-201-M2 | Lvgo cooler - fan motor 2/2 | 0.48 | 23.3 | 225 | layout | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 3.86 | 11.07 | 0.36 | 11.43 | 2.7 | MCCB 45 A (125 AF) + DOL, NEMA size 2
84 | CBL-A-202-M1 | MCC-101A | A-202-M1 | Hvgo Product cooler - fan motor 1/2 | 0.48 | 55.3 | 230 | layout | 3C x 25 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 25 | 1 | 92.5 | 3.88 | 12.1 | 0.85 | 12.95 | 4.9 | MCCB 100 A (125 AF) + DOL, NEMA size 3
85 | CBL-A-202-M2 | MCC-101B | A-202-M2 | Hvgo Product cooler - fan motor 2/2 | 0.48 | 55.3 | 230 | layout | 3C x 25 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 25 | 1 | 92.5 | 3.88 | 12.1 | 0.85 | 12.95 | 4.9 | MCCB 100 A (125 AF) + DOL, NEMA size 3
86 | CBL-X-101-PA | MCC-101A | X-101-PA | Demulsifier injection package - metering pump A | 0.48 | 1.5 | 95 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.23 | 0.71 | 0.02 | 0.73 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
87 | CBL-X-101-PB | MCC-101B | X-101-PB | Demulsifier injection package - metering pump B | 0.48 | 1.5 | 95 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.23 | 0.71 | 0.02 | 0.73 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
88 | CBL-X-102-PA | MCC-101A | X-102-PA | Caustic injection package (desalted crude) - metering pump A | 0.48 | 1.5 | 95 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.23 | 0.71 | 0.02 | 0.73 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
89 | CBL-X-102-PB | MCC-101B | X-102-PB | Caustic injection package (desalted crude) - metering pump B | 0.48 | 1.5 | 95 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.23 | 0.71 | 0.02 | 0.73 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
90 | CBL-X-103-PA | MCC-101A | X-103-PA | Neutraliser / filming amine package (atm OH) - metering pump A | 0.48 | 1.5 | 160 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.39 | 1.19 | 0.02 | 1.22 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
91 | CBL-X-103-PB | MCC-101B | X-103-PB | Neutraliser / filming amine package (atm OH) - metering pump B | 0.48 | 1.5 | 160 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.39 | 1.19 | 0.02 | 1.22 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
92 | CBL-X-104-PA | MCC-101A | X-104-PA | Corrosion inhibitor package (VDU OH) - metering pump A | 0.48 | 1.5 | 295 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.72 | 2.2 | 0.02 | 2.22 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
93 | CBL-X-104-PB | MCC-101B | X-104-PB | Corrosion inhibitor package (VDU OH) - metering pump B | 0.48 | 1.5 | 295 | layout | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.72 | 2.2 | 0.02 | 2.22 | 1.6 | MCCB 15 A (125 AF) + DOL, NEMA size 0
94 | CBL-DT-101A1 | MCC-101A | DT-101A1 | D-101A 1st stage - HV transformer 1/2 (150 kVA, 480 V / 13-23 kV) | 0.48 | 180.4 | 70 | layout | 3C x 120 + E70 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 120 | 1 | 251.9 | 0.95 |  |  |  | 8.6 | MCCB 250 A (250 AF) - desalter transformer feeder
95 | CBL-DT-101A2 | MCC-101B | DT-101A2 | D-101A 1st stage - HV transformer 2/2 (150 kVA, 480 V / 13-23 kV) | 0.48 | 180.4 | 70 | layout | 3C x 120 + E70 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 120 | 1 | 251.9 | 0.95 |  |  |  | 8.6 | MCCB 250 A (250 AF) - desalter transformer feeder
96 | CBL-DT-101B1 | MCC-101A | DT-101B1 | D-101B 2nd stage - HV transformer 1/2 (150 kVA, 480 V / 13-23 kV) | 0.48 | 180.4 | 60 | layout | 3C x 120 + E70 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 120 | 1 | 251.9 | 0.81 |  |  |  | 8.6 | MCCB 250 A (250 AF) - desalter transformer feeder
97 | CBL-DT-101B2 | MCC-101B | DT-101B2 | D-101B 2nd stage - HV transformer 2/2 (150 kVA, 480 V / 13-23 kV) | 0.48 | 180.4 | 60 | layout | 3C x 120 + E70 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 120 | 1 | 251.9 | 0.81 |  |  |  | 8.6 | MCCB 250 A (250 AF) - desalter transformer feeder
98 | CBL-MOV-A | MCC-101A | MOV-A | MOV / electric valve actuators - allowance (18 x 1.5 kW), bus A | 0.48 | 43.3 | 170 | area:PLOT | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 4.82 |  |  |  | 2.7 | MCCB 60 A (125 AF)
99 | CBL-MOV-B | MCC-101B | MOV-B | MOV / electric valve actuators - allowance (18 x 1.5 kW), bus B | 0.48 | 43.3 | 170 | area:PLOT | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 4.82 |  |  |  | 2.7 | MCCB 60 A (125 AF)
100 | CBL-HTP-101 | MCC-101A | HTP-101 | Electric heat tracing panel - CDU slop & HN lines (allowance) | 0.48 | 36.1 | 170 | area:CDU_P | 3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 16 | 1 | 72.8 | 3.26 |  |  |  | 2.7 | MCCB 50 A (125 AF)
101 | CBL-HTP-102 | MCC-101B | HTP-102 | Electric heat tracing panel - VDU slop wax / slop oil lines (allowance) | 0.48 | 48.1 | 250 | area:VDU_P | 3C x 25 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 25 | 1 | 92.5 | 4.04 |  |  |  | 4.9 | MCCB 70 A (125 AF)
102 | CBL-AH-101 | MCC-101B | AH-101 | Analyser house AH-101 HVAC & utilities (analysers on UPS) | 0.48 | 21.2 | 190 | area:CDU | 3C x 6 + E6 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 6 | 1 | 39.3 | 4.94 |  |  |  | 1.6 | MCCB 30 A (125 AF)
103 | CBL-BEF-101A | MCC-101A | BEF-101A | SS-100 battery-room exhaust fan A | 0.48 | 1.7 | 20 | inside SS-100 | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.06 |  |  |  | 1.6 | MCCB 15 A (125 AF)
104 | CBL-BEF-101B | MCC-101B | BEF-101B | SS-100 battery-room exhaust fan B | 0.48 | 1.7 | 20 | inside SS-100 | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.06 |  |  |  | 1.6 | MCCB 15 A (125 AF)
105 | CBL-HVAC-101A | MCC-101A | HVAC-101A | SS-100 HVAC package A (2 x 100 %) | 0.48 | 84.9 | 20 | inside SS-100 | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 0.38 |  |  |  | 4.9 | MCCB 110 A (125 AF)
106 | CBL-HVAC-101B | MCC-101B | HVAC-101B | SS-100 HVAC package B (2 x 100 %) | 0.48 | 84.9 | 20 | inside SS-100 | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 0.38 |  |  |  | 4.9 | MCCB 110 A (125 AF)
107 | CBL-HVAC-102A | MCC-101A | HVAC-102A | FAR-100 HVAC package A (2 x 100 %) | 0.48 | 35.4 | 50 | FAR-100 | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 1.3 |  |  |  | 2.7 | MCCB 45 A (125 AF)
108 | CBL-HVAC-102B | MCC-101B | HVAC-102B | FAR-100 HVAC package B (2 x 100 %) | 0.48 | 35.4 | 50 | FAR-100 | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 1.3 |  |  |  | 2.7 | MCCB 45 A (125 AF)
109 | CBL-WR-A | MCC-101A | WR-A | Welding receptacles 3 x 63 A, 480 V, bus A | 0.48 | 128.9 | 170 | area:PLOT | 3C x 70 + E35 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 70 | 1 | 179.1 | 2.34 |  |  |  | 8.6 | MCCB 175 A (250 AF)
110 | CBL-WR-B | MCC-101B | WR-B | Welding receptacles 3 x 63 A, 480 V, bus B | 0.48 | 128.9 | 170 | area:PLOT | 3C x 70 + E35 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 70 | 1 | 179.1 | 2.34 |  |  |  | 8.6 | MCCB 175 A (250 AF)
111 | CBL-CP-101 | MCC-101A | CP-101 | Cathodic protection transformer-rectifier (buried piping / tank bottoms in plot) | 0.48 | 12 | 60 | area:DESALT | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 1.24 |  |  |  | 1.6 | MCCB 20 A (125 AF)
112 | CBL-BC-101A | MCC-101A | BC-101A | 125 V DC battery charger A (switchgear control), 2 x 100 % | 0.48 | 9.4 | 20 | inside SS-100 | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.34 |  |  |  | 1.6 | MCCB 15 A (125 AF)
113 | CBL-BC-101B | MCC-101B | BC-101B | 125 V DC battery charger B (switchgear control), 2 x 100 % | 0.48 | 9.4 | 20 | inside SS-100 | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 0.34 |  |  |  | 1.6 | MCCB 15 A (125 AF)
114 | CBL-UPS-101A | MCC-101A | UPS-101A | UPS-101A rectifier input (2 x 100 % 100 kVA, 50 % share + battery recharge) | 0.48 | 43.1 | 20 | inside SS-100 | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 0.7 |  |  |  | 2.7 | MCCB 60 A (125 AF)
115 | CBL-UPS-101B | MCC-101B | UPS-101B | UPS-101B rectifier input (2 x 100 % 100 kVA, 50 % share + battery recharge) | 0.48 | 43.1 | 20 | inside SS-100 | 3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 10 | 1 | 54.6 | 0.7 |  |  |  | 2.7 | MCCB 60 A (125 AF)
116 | CBL-HST-101 | MCC-101A | HST-101 | Monorail hoists P-101/P-102 maintenance (2 x 7.5 kW) | 0.48 | 22.6 | 85 | area:DESALT_P | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 3.3 |  |  |  | 1.6 | MCCB 30 A (125 AF)
117 | CBL-SB-101 | MCC-101B | SB-101 | H-101 convection sootblowers (8 x 0.75 kW, electric retract) | 0.48 | 9 | 120 | area:H101 | 3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 4 | 1 | 30.6 | 1.86 |  |  |  | 1.6 | MCCB 15 A (125 AF)
118 | CBL-LTR-101A | MCC-101A | LTR-101A (75 kVA 480-208Y/120 V) | Lighting & small-power transformer -> LDB-101A | 0.48 | 90.2 | 20 | inside SS-100 | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 0.43 |  |  |  | 4.9 | MCCB 125 A (125 AF)
119 | CBL-LTR-101B | MCC-101B | LTR-101B (75 kVA 480-208Y/120 V) | Lighting & small-power transformer -> LDB-101B | 0.48 | 90.2 | 20 | inside SS-100 | 3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 35 | 1 | 115 | 0.43 |  |  |  | 4.9 | MCCB 125 A (125 AF)
TOTAL LENGTH (m)

## Quantities
100 kBPSD Crude & Vacuum Distillation Unit - Cable Quantities by Type (length x parallel runs)
CFU-000-EL-CBL-001 Rev A (Issued for review (FEED)), 2026-10-02 ¦ Generic Refinery - Gulf Coast
Cable type | Total length (m) | With 10 % wastage (m)
1 x (3 x 1C x 240 mm2) Cu/XLPE/CWS/PVC 8.7/15 kV, trefoil | 1260 | 1386
2 x (3 x 1C x 500 mm2) Cu/XLPE/CWS/PVC 3.6/6 kV, trefoil | 100 | 110
2 x 3C x 150 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 120 | 132
3C x 10 + E10 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 1290 | 1419
3C x 120 + E70 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 585 | 643.5
3C x 150 + E95 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 515 | 566.5
3C x 16 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 1405 | 1545.5
3C x 185 + E95 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 285 | 313.5
3C x 240 + E120 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 865 | 951.5
3C x 25 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 1320 | 1452
3C x 35 + 3E x 11.6667 mm2 Cu/XLPE/CWS/SWA/PVC 0.6/1 kV, symmetrical VFD cable | 870 | 957
3C x 35 + E16 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 925 | 1017.5
3C x 4 + E4 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 3890 | 4279
3C x 6 + E6 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 1265 | 1391.5
3C x 70 + E35 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 900 | 990
3C x 70 mm2 Cu/XLPE/CWS/SWA/PVC 3.6/6 kV | 1420 | 1562
3C x 95 + E50 mm2 Cu/XLPE/SWA/PVC 0.6/1 kV | 380 | 418
Non-segregated phase bus duct 5000 A, Cu, 65 kA | 30 | 33

## Basis
100 kBPSD Crude & Vacuum Distillation Unit - Cable Sizing Basis
CFU-000-EL-CBL-001 Rev A (Issued for review (FEED)), 2026-10-02 ¦ Generic Refinery - Gulf Coast
1. Conductors: copper, XLPE 90 C, IEC 60228 metric sizes (mm2). LV 0.6/1 kV Cu/XLPE/SWA/PVC multicore with separate earth core (IEC 60364-5-54 sizing); 4.16 kV: 3.6/6 kV screened 3-core Cu/XLPE/CWS/SWA/PVC; 13.8 kV: 8.7/15 kV single-core in trefoil. Equivalent UL/NEC types (MC-HL / TC-ER) acceptable; NEC 310 ampacity check at detailed design.
2. Ampacity: base values IEC 60364-5-52 Table B.52.12 method E (LV) / IEC 60502-2 Annex B (MV) at 30 C in air on ladder tray; derating 0.91 (40 C ambient incl. solar) x 0.8 (grouping) = 0.73. Required ampacity >= 1.25 x FLC for motors (NEC 430.22) and >= 1.25 x rated current for feeders (continuous load).
3. Voltage drop: dV% = sqrt(3) I L (R cos(phi) + X sin(phi)) / V x 100 with R at 90 C. Running <= 5 %. Starting (DOL, 6.5 x FLC at PF 0.35 LV / 0.2 MV): bus dip + cable drop <= 15 % at motor terminals; bus dip <= 10 %.
4. Short-circuit withstand: S >= sqrt(I^2 t) / k, k = 143 (Cu/XLPE 90->250 C). MV: prospective bus fault current with t = 0.25 s (motor feeders, instantaneous 50 element) / 0.5 s (incomers, transformer feeders). LV: let-through I^2t of current-limiting MCCB by rating (manufacturer typical, 65 kA class).
5. Minimum sizes: LV power 4 mm2; 4.16 kV 35 mm2. Parallel LV runs >= 95 mm2.
6. Route length = Manhattan distance from SS-100 reference point (25, 12.5) m to the consumer + 15 m riser/termination allowance (+10 m for air-cooler fan motors on top of the pipe rack), rounded up to 5 m. Coordinates source: data/layout.json (141 tagged items).
7. 13.8 kV incomer route from the refinery main substation assumed 600 m (OSBL, to be confirmed by refinery electrical master plan).