## Instrument Index
INSTRUMENT INDEX
CFU-000-IC-IDX-001 Rev A - Issued for review (FEED) 2026-10-02 100 kBPSD CDU/VDU
Tag | Type | Loop | Service | P&ID | System | Signal | Range | Units | Fail pos. | SIF | SIL | Line No. | Note
FE-1001 | Flow element (orifice) | FIC-1001 | Crude charge orifice | CFU-100-PR-PID-001 | Local | - (local / mechanical) | [5 empty] | 12"-P-100-002-B1-N
FIC-1001 | Flow indicating controller | FIC-1001 | Crude charge flow (unit throughput) | CFU-100-PR-PID-001 | DCS | Soft (DCS function block) | 0-1000 | m3/h |  |  |  | 12"-P-100-002-B1-N
FT-1001 | Flow transmitter | FIC-1001 | Crude charge flow (unit throughput) | CFU-100-PR-PID-001 | DCS | 4-20 mA HART | 0-1000 | m3/h |  |  |  | 12"-P-100-002-B1-N
FV-1001 | Flow control valve | FIC-1001 | Crude charge flow (unit throughput) | CFU-100-PR-PID-001 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 12"-P-100-002-B1-N
PSV-1001 | Pressure safety valve | PSV-1001 |  | CFU-100-PR-PID-007 | Local | - (local / mechanical) | Set 2.4 | barg
XV-1001 | On/off shutdown valve | FIC-1001 | C-101 high-high bottom level -> stop P-101 / close FV-1001 | CFU-100-PR-PID-001 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-108 | SIL 1 | 12"-P-100-002-B1-N
FFIC-1002 | Flow ratio controller | FFIC-1002 | Demulsifier injection ratio to crude | CFU-100-PR-PID-001 | DCS | Soft (DCS function block) | 0-2 | ratio
FY-1002 | Flow relay / stroke positioner | FFIC-1002 | Demulsifier pump stroke positioner | CFU-100-PR-PID-001 | DCS | 4-20 mA AO
PSV-1002 | Pressure safety valve | PSV-1002 |  | CFU-100-PR-PID-002 | Local | - (local / mechanical) | Set 15.5 | barg
FFIC-1003 | Flow ratio controller | FFIC-1003 | Wash water ratio to crude (5 LV%) | CFU-100-PR-PID-002 | DCS | Soft (DCS function block) | 0-2 | ratio |  |  |  | 3"-WW-100-028-A3-P
FT-1003 | Flow transmitter | FFIC-1003 | Wash water ratio to crude (5 LV%) | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-50 | m3/h |  |  |  | 3"-WW-100-028-A3-P
FV-1003 | Flow control valve | FFIC-1003 | Wash water ratio to crude (5 LV%) | CFU-100-PR-PID-002 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 3"-WW-100-028-A3-P
PSV-1003 | Pressure safety valve | PSV-1003 |  | CFU-100-PR-PID-002 | Local | - (local / mechanical) | Set 15.5 | barg
PSV-1004 | Pressure safety valve | PSV-1004 |  | CFU-100-PR-PID-009 | Local | - (local / mechanical) | Set 2.4 | barg
TIC-1004 | Temperature indicating controller | TIC-1004 | Desalter inlet temperature | CFU-100-PR-PID-001 | DCS | Soft (DCS function block) | 0-200 | C |  |  |  | 12"-P-100-009-B1-H
TT-1004 | Temperature transmitter | TIC-1004 | Desalter inlet temperature | CFU-100-PR-PID-001 | DCS | 4-20 mA HART | 0-200 | C |  |  |  | 12"-P-100-009-B1-H
TV-1004 | Temperature control valve | TIC-1004 | Desalter inlet temperature | CFU-100-PR-PID-001 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 12"-P-100-009-B1-H
PDIC-1005 | Differential pressure indicating controller | PDIC-1005 | 1st-stage mix valve dP | CFU-100-PR-PID-002 | DCS | Soft (DCS function block) | 0-2.5 | bar |  |  |  | 12"-P-100-009-B1-H
PDT-1005 | Differential pressure transmitter | PDIC-1005 | 1st-stage mix valve dP | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-2.5 | bar |  |  |  | 12"-P-100-009-B1-H
PDV-1005 | Differential pressure control (mix) valve | PDIC-1005 | 1st-stage mix valve dP | CFU-100-PR-PID-002 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 12"-P-100-009-B1-H
PSV-1005 | Pressure safety valve | PSV-1005 |  | CFU-100-PR-PID-010 | Local | - (local / mechanical) | Set 13.0 | barg
PDIC-1006 | Differential pressure indicating controller | PDIC-1006 | 2nd-stage mix valve dP | CFU-100-PR-PID-002 | DCS | Soft (DCS function block) | 0-2.5 | bar |  |  |  | 12"-P-100-021-B1-H
PDT-1006 | Differential pressure transmitter | PDIC-1006 | 2nd-stage mix valve dP | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-2.5 | bar |  |  |  | 12"-P-100-021-B1-H
PDV-1006 | Differential pressure control (mix) valve | PDIC-1006 | 2nd-stage mix valve dP | CFU-100-PR-PID-002 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 12"-P-100-021-B1-H
PSV-1006 | Pressure safety valve | PSV-1006 |  | CFU-100-PR-PID-010 | Local | - (local / mechanical) | Set 15.2 | barg
LIC-1007 | Level indicating controller | LIC-1007 | D-101A water/oil interface | CFU-100-PR-PID-002 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 3"-WW-100-030-A3-P
LT-1007 | Level transmitter | LIC-1007 | D-101A water/oil interface | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 3"-WW-100-030-A3-P
LT-1007B | Level transmitter | LIC-1007 | D-101A/B low-low interface (grid short) -> trip transformers | CFU-100-PR-PID-002 | SIS | 4-20 mA HART (SIS AI) | 0-100 | % |  | SIF-107 | SIL 1 | 3"-WW-100-030-A3-P
LV-1007 | Level control valve | LIC-1007 | D-101A water/oil interface | CFU-100-PR-PID-002 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 3"-WW-100-030-A3-P
LZLL-1007 | Level low-low trip function (SIS) | LIC-1007 | D-101A/B low-low interface (grid short) -> trip transformers | CFU-100-PR-PID-002 | SIS | Soft (SIS logic) | 0-100 | % |  | SIF-107 | SIL 1 | 3"-WW-100-030-A3-P
PSV-1007 | Pressure safety valve | PSV-1007 |  | CFU-100-PR-PID-011 | Local | - (local / mechanical) | Set 3.5 | barg
XY-1007 | Trip relay output | LIC-1007 | D-101A transformer feeder trip | CFU-100-PR-PID-002 | SIS | DO 24 VDC (interposing relay) |  |  |  | SIF-107 | SIL 1 | 3"-WW-100-030-A3-P
LIC-1008 | Level indicating controller | LIC-1008 | D-101B water/oil interface | CFU-100-PR-PID-002 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 3"-WW-100-029-A3-P
LT-1008 | Level transmitter | LIC-1008 | D-101B water/oil interface | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 3"-WW-100-029-A3-P
LT-1008B | Level transmitter | LIC-1008 | D-101A/B low-low interface (grid short) -> trip transformers | CFU-100-PR-PID-002 | SIS | 4-20 mA HART (SIS AI) | 0-100 | % |  | SIF-107 | SIL 1 | 3"-WW-100-029-A3-P
LV-1008 | Level control valve | LIC-1008 | D-101B water/oil interface | CFU-100-PR-PID-002 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 3"-WW-100-029-A3-P
LZLL-1008 | Level low-low trip function (SIS) | LIC-1008 | D-101A/B low-low interface (grid short) -> trip transformers | CFU-100-PR-PID-002 | SIS | Soft (SIS logic) | 0-100 | % |  | SIF-107 | SIL 1 | 3"-WW-100-029-A3-P
PSV-1008 | Pressure safety valve | PSV-1008 |  | CFU-100-PR-PID-010 | Local | - (local / mechanical) | Set 13.0 | barg
XY-1008 | Trip relay output | LIC-1008 | D-101B transformer feeder trip | CFU-100-PR-PID-002 | SIS | DO 24 VDC (interposing relay) |  |  |  | SIF-107 | SIL 1 | 3"-WW-100-029-A3-P
PIC-1009 | Pressure indicating controller | PIC-1009 | Desalter pressure (above crude vapour pressure) | CFU-100-PR-PID-002 | DCS | Soft (DCS function block) | 0-15 | barg |  |  |  | 20"-P-100-022-B1-H
PSV-1009 | Pressure safety valve | PSV-1009 |  | CFU-100-PR-PID-008 | Local | - (local / mechanical) | Set 3.5 | barg
PT-1009 | Pressure transmitter | PIC-1009 | Desalter pressure (above crude vapour pressure) | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-15 | barg |  |  |  | 20"-P-100-022-B1-H
PV-1009 | Pressure control valve | PIC-1009 | Desalter pressure (above crude vapour pressure) | CFU-100-PR-PID-002 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 20"-P-100-022-B1-H
FFIC-1010 | Flow ratio controller | FFIC-1010 | Caustic injection ratio | CFU-100-PR-PID-002 | DCS | Soft (DCS function block) | 0-2 | ratio
PSV-1010 | Pressure safety valve | PSV-1010 |  | CFU-100-PR-PID-001 | Local | - (local / mechanical) | Set 30.0 | barg
FE-1011 | Flow element (orifice) | FIC-1011 | H-101 pass 1 flow element | CFU-100-PR-PID-004 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-059-B2-H
FIC-1011 | Flow indicating controller | FIC-1011 | H-101 pass 1 flow | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-100000 | kg/h |  |  |  | 6"-P-100-059-B2-H
FT-1011 | Flow transmitter | FIC-1011 | H-101 pass 1 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-100000 | kg/h |  |  |  | 6"-P-100-059-B2-H
FT-1011A | Flow transmitter | FIC-1011 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-059-B2-H
FT-1011B | Flow transmitter | FIC-1011 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-059-B2-H
FT-1011C | Flow transmitter | FIC-1011 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-059-B2-H
FV-1011 | Flow control valve | FIC-1011 | H-101 pass 1 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-100-059-B2-H
FZLL-1011 | Flow low-low trip function (SIS) | FIC-1011 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | Soft (SIS logic) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-059-B2-H
PSV-1011 | Pressure safety valve | PSV-1011 |  | CFU-100-PR-PID-003 | Local | - (local / mechanical) | Set 12.0 | barg
TI-1011 | Temperature indicator | FIC-1011 | H-101 pass 1 outlet temperature | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 8"-P-100-067-B3-H
FE-1012 | Flow element (orifice) | FIC-1012 | H-101 pass 2 flow element | CFU-100-PR-PID-004 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-060-B2-H
FIC-1012 | Flow indicating controller | FIC-1012 | H-101 pass 2 flow | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-100000 | kg/h |  |  |  | 6"-P-100-060-B2-H
FT-1012 | Flow transmitter | FIC-1012 | H-101 pass 2 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-100000 | kg/h |  |  |  | 6"-P-100-060-B2-H
FT-1012A | Flow transmitter | FIC-1012 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-060-B2-H
FT-1012B | Flow transmitter | FIC-1012 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-060-B2-H
FT-1012C | Flow transmitter | FIC-1012 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-060-B2-H
FV-1012 | Flow control valve | FIC-1012 | H-101 pass 2 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-100-060-B2-H
FZLL-1012 | Flow low-low trip function (SIS) | FIC-1012 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | Soft (SIS logic) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-060-B2-H
TI-1012 | Temperature indicator | FIC-1012 | H-101 pass 2 outlet temperature | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 8"-P-100-068-B3-H
FE-1013 | Flow element (orifice) | FIC-1013 | H-101 pass 3 flow element | CFU-100-PR-PID-004 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-061-B2-H
FIC-1013 | Flow indicating controller | FIC-1013 | H-101 pass 3 flow | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-100000 | kg/h |  |  |  | 6"-P-100-061-B2-H
FT-1013 | Flow transmitter | FIC-1013 | H-101 pass 3 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-100000 | kg/h |  |  |  | 6"-P-100-061-B2-H
FT-1013A | Flow transmitter | FIC-1013 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-061-B2-H
FT-1013B | Flow transmitter | FIC-1013 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-061-B2-H
FT-1013C | Flow transmitter | FIC-1013 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-061-B2-H
FV-1013 | Flow control valve | FIC-1013 | H-101 pass 3 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-100-061-B2-H
FZLL-1013 | Flow low-low trip function (SIS) | FIC-1013 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | Soft (SIS logic) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-061-B2-H
TI-1013 | Temperature indicator | FIC-1013 | H-101 pass 3 outlet temperature | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 8"-P-100-069-B3-H
FE-1014 | Flow element (orifice) | FIC-1014 | H-101 pass 4 flow element | CFU-100-PR-PID-004 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-062-B2-H
FIC-1014 | Flow indicating controller | FIC-1014 | H-101 pass 4 flow | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-100000 | kg/h |  |  |  | 6"-P-100-062-B2-H
FT-1014 | Flow transmitter | FIC-1014 | H-101 pass 4 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-100000 | kg/h |  |  |  | 6"-P-100-062-B2-H
FT-1014A | Flow transmitter | FIC-1014 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-062-B2-H
FT-1014B | Flow transmitter | FIC-1014 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-062-B2-H
FT-1014C | Flow transmitter | FIC-1014 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-062-B2-H
FV-1014 | Flow control valve | FIC-1014 | H-101 pass 4 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-100-062-B2-H
FZLL-1014 | Flow low-low trip function (SIS) | FIC-1014 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | Soft (SIS logic) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-062-B2-H
TI-1014 | Temperature indicator | FIC-1014 | H-101 pass 4 outlet temperature | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 8"-P-100-070-B3-H
FE-1015 | Flow element (orifice) | FIC-1015 | H-101 pass 5 flow element | CFU-100-PR-PID-004 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-063-B2-H
FIC-1015 | Flow indicating controller | FIC-1015 | H-101 pass 5 flow | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-100000 | kg/h |  |  |  | 6"-P-100-063-B2-H
FT-1015 | Flow transmitter | FIC-1015 | H-101 pass 5 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-100000 | kg/h |  |  |  | 6"-P-100-063-B2-H
FT-1015A | Flow transmitter | FIC-1015 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-063-B2-H
FT-1015B | Flow transmitter | FIC-1015 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-063-B2-H
FT-1015C | Flow transmitter | FIC-1015 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-063-B2-H
FV-1015 | Flow control valve | FIC-1015 | H-101 pass 5 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-100-063-B2-H
FZLL-1015 | Flow low-low trip function (SIS) | FIC-1015 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | Soft (SIS logic) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-063-B2-H
TI-1015 | Temperature indicator | FIC-1015 | H-101 pass 5 outlet temperature | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 8"-P-100-071-B3-H
FE-1016 | Flow element (orifice) | FIC-1016 | H-101 pass 6 flow element | CFU-100-PR-PID-004 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-064-B2-H
FIC-1016 | Flow indicating controller | FIC-1016 | H-101 pass 6 flow | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-100000 | kg/h |  |  |  | 6"-P-100-064-B2-H
FT-1016 | Flow transmitter | FIC-1016 | H-101 pass 6 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-100000 | kg/h |  |  |  | 6"-P-100-064-B2-H
FT-1016A | Flow transmitter | FIC-1016 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-064-B2-H
FT-1016B | Flow transmitter | FIC-1016 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-064-B2-H
FT-1016C | Flow transmitter | FIC-1016 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-064-B2-H
FV-1016 | Flow control valve | FIC-1016 | H-101 pass 6 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-100-064-B2-H
FZLL-1016 | Flow low-low trip function (SIS) | FIC-1016 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | Soft (SIS logic) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-064-B2-H
TI-1016 | Temperature indicator | FIC-1016 | H-101 pass 6 outlet temperature | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 8"-P-100-072-B3-H
FE-1017 | Flow element (orifice) | FIC-1017 | H-101 pass 7 flow element | CFU-100-PR-PID-004 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-065-B2-H
FIC-1017 | Flow indicating controller | FIC-1017 | H-101 pass 7 flow | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-100000 | kg/h |  |  |  | 6"-P-100-065-B2-H
FT-1017 | Flow transmitter | FIC-1017 | H-101 pass 7 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-100000 | kg/h |  |  |  | 6"-P-100-065-B2-H
FT-1017A | Flow transmitter | FIC-1017 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-065-B2-H
FT-1017B | Flow transmitter | FIC-1017 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-065-B2-H
FT-1017C | Flow transmitter | FIC-1017 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-065-B2-H
FV-1017 | Flow control valve | FIC-1017 | H-101 pass 7 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-100-065-B2-H
FZLL-1017 | Flow low-low trip function (SIS) | FIC-1017 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | Soft (SIS logic) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-065-B2-H
TI-1017 | Temperature indicator | FIC-1017 | H-101 pass 7 outlet temperature | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 8"-P-100-073-B3-H
FE-1018 | Flow element (orifice) | FIC-1018 | H-101 pass 8 flow element | CFU-100-PR-PID-004 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-066-B2-H
FIC-1018 | Flow indicating controller | FIC-1018 | H-101 pass 8 flow | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-100000 | kg/h |  |  |  | 6"-P-100-066-B2-H
FT-1018 | Flow transmitter | FIC-1018 | H-101 pass 8 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-100000 | kg/h |  |  |  | 6"-P-100-066-B2-H
FT-1018A | Flow transmitter | FIC-1018 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-066-B2-H
FT-1018B | Flow transmitter | FIC-1018 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-066-B2-H
FT-1018C | Flow transmitter | FIC-1018 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-066-B2-H
FV-1018 | Flow control valve | FIC-1018 | H-101 pass 8 flow | CFU-100-PR-PID-004 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-100-066-B2-H
FZLL-1018 | Flow low-low trip function (SIS) | FIC-1018 | H-101 low-low pass flow (any pass) -> trip fuel | CFU-100-PR-PID-004 | SIS | Soft (SIS logic) | 0-100000 | kg/h |  | SIF-101 | SIL 2 | 6"-P-100-066-B2-H
TI-1018 | Temperature indicator | FIC-1018 | H-101 pass 8 outlet temperature | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 8"-P-100-074-B3-H
TDIC-1019 | Temperature differential controller | TDIC-1019 | H-101 pass outlet temperature balancing | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | -50-50 | C
TIC-1020 | Temperature indicating controller | TIC-1020 | H-101 coil outlet temperature (COT) | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-500 | C |  |  |  | 28"-P-100-075-B3-H
TT-1020 | Temperature transmitter | TIC-1020 | H-101 coil outlet temperature (COT) | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 28"-P-100-075-B3-H
TT-1020A | Temperature transmitter | TIC-1020 | H-101 high-high COT -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-500 | C |  | SIF-106 | SIL 1 | 28"-P-100-075-B3-H
TT-1020B | Temperature transmitter | TIC-1020 | H-101 high-high COT -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-500 | C |  | SIF-106 | SIL 1 | 28"-P-100-075-B3-H
TT-1020C | Temperature transmitter | TIC-1020 | H-101 high-high COT -> trip fuel | CFU-100-PR-PID-004 | SIS | 4-20 mA HART (SIS AI) | 0-500 | C |  | SIF-106 | SIL 1 | 28"-P-100-075-B3-H
TZHH-1020 | Temperature high-high trip function (SIS) | TIC-1020 | H-101 high-high COT -> trip fuel (2oo3) | CFU-100-PR-PID-004 | SIS | Soft (SIS logic) | 0-500 | C |  | SIF-106 | SIL 1 | 28"-P-100-075-B3-H
PIC-1021 | Pressure indicating controller | PIC-1021 | H-101 fuel gas burner pressure | CFU-100-PR-PID-005 | DCS | Soft (DCS function block) | 0-4 | barg |  |  |  | 10"-FG-100-080-A1-N
PT-1021 | Pressure transmitter | PIC-1021 | H-101 fuel gas burner pressure | CFU-100-PR-PID-005 | DCS | 4-20 mA HART | 0-4 | barg |  |  |  | 10"-FG-100-080-A1-N
PV-1021 | Pressure control valve | PIC-1021 | H-101 fuel gas burner pressure | CFU-100-PR-PID-005 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 10"-FG-100-080-A1-N
XV-1021 | On/off shutdown valve | PIC-1021 | H-101 main fuel gas SSOV | CFU-100-PR-PID-005 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-101 | SIL 2 | 10"-FG-100-080-A1-N
AIC-1022 | Analyser indicating controller | AIC-1022 | H-101 flue gas O2 (excess-air trim) | CFU-100-PR-PID-005 | DCS | Soft (DCS function block) | 0-10 | vol% O2
AT-1022 | Analyser transmitter | AIC-1022 | H-101 arch O2 / CO analyser | CFU-100-PR-PID-005 | DCS | 4-20 mA HART | 0-10 | vol% O2
XV-1022 | On/off shutdown valve | AIC-1022 | H-101 main fuel gas SSOV | CFU-100-PR-PID-005 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-101 | SIL 2
PIC-1023 | Pressure indicating controller | PIC-1023 | H-101 arch draft | CFU-100-PR-PID-005 | DCS | Soft (DCS function block) | -25-25 | mmH2O
PT-1023 | Pressure transmitter | PIC-1023 | H-101 arch draft | CFU-100-PR-PID-005 | DCS | 4-20 mA HART | -25-25 | mmH2O
PV-1023 | Pressure control valve | PIC-1023 | H-101 stack damper actuator | CFU-100-PR-PID-005 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO
PY-1023 | Pressure relay / VSD signal | PIC-1023 | ID fan VSD speed signal / stack damper | CFU-100-PR-PID-005 | DCS | 4-20 mA AO
TIC-1024 | Temperature indicating controller | TIC-1024 | Stripping-steam superheat outlet | CFU-100-PR-PID-004 | DCS | Soft (DCS function block) | 0-500 | C |  |  |  | 12"-LS-100-077-S1-H
TT-1024 | Temperature transmitter | TIC-1024 | Stripping-steam superheat outlet | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 12"-LS-100-077-S1-H
TV-1024 | Temperature control valve | TIC-1024 | Stripping-steam superheat outlet | CFU-100-PR-PID-004 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 12"-LS-100-077-S1-H
FE-1025 | Flow element (orifice) | FIC-1025 | H-101 combustion air flow element (venturi) | CFU-100-PR-PID-005 | Local | - (local / mechanical)
FIC-1025 | Flow indicating controller | FIC-1025 | H-101 combustion air flow | CFU-100-PR-PID-005 | DCS | Soft (DCS function block) | 0-100 | %
FT-1025 | Flow transmitter | FIC-1025 | H-101 combustion air flow | CFU-100-PR-PID-005 | DCS | 4-20 mA HART | 0-100 | %
FV-1025 | Flow control valve | FIC-1025 | H-101 FD fan inlet vanes (FIC-1025) | CFU-100-PR-PID-005 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO
XV-1026 | On/off shutdown valve | XV-1026 | H-101 pilot gas SSOV | CFU-100-PR-PID-005 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-101 | SIL 2
PT-1027A | Pressure transmitter | PT-1027A | H-101 low-low fuel gas pressure -> trip fuel | CFU-100-PR-PID-005 | SIS | 4-20 mA HART (SIS AI) | 0-5 | barg |  | SIF-102 | SIL 1
PT-1027B | Pressure transmitter | PT-1027B | H-101 low-low fuel gas pressure -> trip fuel | CFU-100-PR-PID-005 | SIS | 4-20 mA HART (SIS AI) | 0-5 | barg |  | SIF-102 | SIL 1
PT-1027C | Pressure transmitter | PT-1027C | H-101 low-low fuel gas pressure -> trip fuel | CFU-100-PR-PID-005 | SIS | 4-20 mA HART (SIS AI) | 0-5 | barg |  | SIF-102 | SIL 1
PZHH-1027 | Pressure high-high trip function (SIS) | PZHH-1027 | H-101 high-high fuel gas pressure -> trip fuel | CFU-100-PR-PID-005 | SIS | Soft (SIS logic) | 0-5 | barg |  | SIF-103 | SIL 1
PZLL-1027 | Pressure low-low trip function (SIS) | PZLL-1027 | H-101 low-low fuel gas pressure -> trip fuel (2oo3) | CFU-100-PR-PID-005 | SIS | Soft (SIS logic) | 0-5 | barg |  | SIF-102 | SIL 1
BS-1028 | Flame scanner | BS-1028 | H-101 flame scanners (1 per burner, 16 off) | CFU-100-PR-PID-005 | DCS | DI 24 VDC | Flame ON/OFF | -
BZLL-1028 | Flame failure trip function (SIS) | BZLL-1028 | Loss of flame (all burners) | CFU-100-PR-PID-005 | SIS | Soft (SIS logic) | Flame ON/OFF | - |  | SIF-104 | SIL 2
PT-1029A | Pressure transmitter | PT-1029A | H-101 high-high arch pressure / loss of ID fan -> trip | CFU-100-PR-PID-005 | SIS | 4-20 mA HART (SIS AI) | -25-25 | mmH2O |  | SIF-105 | SIL 1
PT-1029B | Pressure transmitter | PT-1029B | H-101 high-high arch pressure / loss of ID fan -> trip | CFU-100-PR-PID-005 | SIS | 4-20 mA HART (SIS AI) | -25-25 | mmH2O |  | SIF-105 | SIL 1
PT-1029C | Pressure transmitter | PT-1029C | H-101 high-high arch pressure / loss of ID fan -> trip | CFU-100-PR-PID-005 | SIS | 4-20 mA HART (SIS AI) | -25-25 | mmH2O |  | SIF-105 | SIL 1
PZHH-1029 | Pressure high-high trip function (SIS) | PZHH-1029 | H-101 high-high arch pressure / loss of ID fan -> trip (2oo3) | CFU-100-PR-PID-005 | SIS | Soft (SIS logic) | -25-25 | mmH2O |  | SIF-105 | SIL 1
TIC-1030 | Temperature indicating controller | TIC-1030 | C-101 top temperature (naphtha end point) | CFU-100-PR-PID-007 | DCS | Soft (DCS function block) | 0-200 | C |  |  |  | 36"-PG-100-107-A2-H
TT-1030 | Temperature transmitter | TIC-1030 | C-101 top temperature (naphtha end point) | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-200 | C |  |  |  | 36"-PG-100-107-A2-H
FE-1031 | Flow element (orifice) | FIC-1031 | Reflux flow element | CFU-100-PR-PID-009 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-111-A1-N
FIC-1031 | Flow indicating controller | FIC-1031 | C-101 reflux | CFU-100-PR-PID-009 | DCS | Soft (DCS function block) | 0-200 | m3/h |  |  |  | 6"-P-100-111-A1-N
FT-1031 | Flow transmitter | FIC-1031 | C-101 reflux | CFU-100-PR-PID-009 | DCS | 4-20 mA HART | 0-200 | m3/h |  |  |  | 6"-P-100-111-A1-N
FV-1031 | Flow control valve | FIC-1031 | C-101 reflux | CFU-100-PR-PID-009 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-P-100-111-A1-N
PIC-1032 | Pressure indicating controller | PIC-1032 | OH drum pressure (split range) | CFU-100-PR-PID-009 | DCS | Soft (DCS function block) | 0-3 | barg |  |  |  | 6"-PG-100-116-A2-N
PT-1032 | Pressure transmitter | PIC-1032 | OH drum pressure (split range) | CFU-100-PR-PID-009 | DCS | 4-20 mA HART | 0-3 | barg |  |  |  | 6"-PG-100-116-A2-N
PV-1032A | Pressure control valve | PIC-1032 | OH drum pressure (split range) | CFU-100-PR-PID-009 | DCS | 4-20 mA HART AO (smart positioner) | [5 empty] | 6"-PG-100-116-A2-N
LAHH-1033 | Level alarm high-high (DCS) | LIC-1033 | D-102 hydrocarbon level high-high alarm (DCS only) | CFU-100-PR-PID-009 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 10"-P-100-112-A2-N
LIC-1033 | Level indicating controller | LIC-1033 | D-102 hydrocarbon level | CFU-100-PR-PID-009 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 10"-P-100-112-A2-N
LT-1033 | Level transmitter | LIC-1033 | D-102 hydrocarbon level | CFU-100-PR-PID-009 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 10"-P-100-112-A2-N
FE-1034 | Flow element (orifice) | FIC-1034 | Unstabilised naphtha flow element | CFU-100-PR-PID-009 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-113-B1-N
FIC-1034 | Flow indicating controller | FIC-1034 | Unstabilised naphtha to C-105 | CFU-100-PR-PID-009 | DCS | Soft (DCS function block) | 0-250 | m3/h |  |  |  | 6"-P-100-113-B1-N
FT-1034 | Flow transmitter | FIC-1034 | Unstabilised naphtha to C-105 | CFU-100-PR-PID-009 | DCS | 4-20 mA HART | 0-250 | m3/h |  |  |  | 6"-P-100-113-B1-N
FV-1034 | Flow control valve | FIC-1034 | Unstabilised naphtha to C-105 | CFU-100-PR-PID-009 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-P-100-113-B1-N
LIC-1035 | Level indicating controller | LIC-1035 | D-102 boot interface | CFU-100-PR-PID-009 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 2"-SW-100-115-A2-N
LT-1035 | Level transmitter | LIC-1035 | D-102 boot interface | CFU-100-PR-PID-009 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 2"-SW-100-115-A2-N
LV-1035 | Level control valve | LIC-1035 | D-102 boot interface | CFU-100-PR-PID-009 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 2"-SW-100-115-A2-N
FFIC-1036 | Flow ratio controller | FFIC-1036 | OH neutraliser ratio / pH | CFU-100-PR-PID-009 | DCS | Soft (DCS function block) | 0-2 | ratio
AIC-1037 | Analyser indicating controller | AIC-1037 | OH sour-water pH | CFU-100-PR-PID-009 | DCS | Soft (DCS function block) | 0-14 | pH
AT-1037 | Analyser transmitter | AIC-1037 | OH sour water pH analyser | CFU-100-PR-PID-009 | DCS | 4-20 mA HART | 0-14 | pH
FE-1040 | Flow element (orifice) | FIC-1040 | TPA flow element | CFU-100-PR-PID-007 | Local | - (local / mechanical) | [5 empty] | 8"-P-100-014-A1-H
FIC-1040 | Flow indicating controller | FIC-1040 | TPA circulation | CFU-100-PR-PID-007 | DCS | Soft (DCS function block) | 0-400 | m3/h |  |  |  | 8"-P-100-014-A1-H
FT-1040 | Flow transmitter | FIC-1040 | TPA circulation | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-400 | m3/h |  |  |  | 8"-P-100-014-A1-H
FV-1040 | Flow control valve | FIC-1040 | TPA circulation | CFU-100-PR-PID-007 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 8"-P-100-014-A1-H
TIC-1041 | Temperature indicating controller | TIC-1041 | TPA return temperature (duty) | CFU-100-PR-PID-001 | DCS | Soft (DCS function block) | 0-150 | C |  |  |  | 8"-P-100-015-A1-H
TT-1041 | Temperature transmitter | TIC-1041 | TPA return temperature (duty) | CFU-100-PR-PID-001 | DCS | 4-20 mA HART | 0-150 | C |  |  |  | 8"-P-100-015-A1-H
TV-1041 | Temperature control valve | TIC-1041 | TPA return temperature (duty) | CFU-100-PR-PID-001 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 8"-P-100-015-A1-H
FE-1042 | Flow element (orifice) | FIC-1042 | MPA flow element | CFU-100-PR-PID-007 | Local | - (local / mechanical) | [5 empty] | 10"-P-100-044-B1-H
FIC-1042 | Flow indicating controller | FIC-1042 | MPA circulation | CFU-100-PR-PID-007 | DCS | Soft (DCS function block) | 0-500 | m3/h |  |  |  | 10"-P-100-044-B1-H
FT-1042 | Flow transmitter | FIC-1042 | MPA circulation | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-500 | m3/h |  |  |  | 10"-P-100-044-B1-H
FV-1042 | Flow control valve | FIC-1042 | MPA circulation | CFU-100-PR-PID-007 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 10"-P-100-044-B1-H
TIC-1043 | Temperature indicating controller | TIC-1043 | MPA return temperature | CFU-100-PR-PID-003 | DCS | Soft (DCS function block) | 0-250 | C |  |  |  | 8"-P-100-045-B1-H
TT-1043 | Temperature transmitter | TIC-1043 | MPA return temperature | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-250 | C |  |  |  | 8"-P-100-045-B1-H
TV-1043 | Temperature control valve | TIC-1043 | MPA return temperature | CFU-100-PR-PID-003 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 8"-P-100-045-B1-H
FE-1044 | Flow element (orifice) | FIC-1044 | BPA flow element | CFU-100-PR-PID-007 | Local | - (local / mechanical) | [5 empty] | 8"-P-100-051-B2-H
FIC-1044 | Flow indicating controller | FIC-1044 | BPA circulation | CFU-100-PR-PID-007 | DCS | Soft (DCS function block) | 0-400 | m3/h |  |  |  | 8"-P-100-051-B2-H
FT-1044 | Flow transmitter | FIC-1044 | BPA circulation | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-400 | m3/h |  |  |  | 8"-P-100-051-B2-H
FV-1044 | Flow control valve | FIC-1044 | BPA circulation | CFU-100-PR-PID-007 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 8"-P-100-051-B2-H
TIC-1045 | Temperature indicating controller | TIC-1045 | BPA return temperature | CFU-100-PR-PID-003 | DCS | Soft (DCS function block) | 0-300 | C |  |  |  | 8"-P-100-053-B1-H
TT-1045 | Temperature transmitter | TIC-1045 | BPA return temperature | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-300 | C |  |  |  | 8"-P-100-053-B1-H
TV-1045 | Temperature control valve | TIC-1045 | BPA return temperature | CFU-100-PR-PID-003 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 8"-P-100-053-B1-H
FE-1050 | Flow element (orifice) | FIC-1050 | C-102 feed (draw) flow element | CFU-100-PR-PID-008 | Local | - (local / mechanical) | [5 empty] | 10"-P-100-092-B1-H
FIC-1050 | Flow indicating controller | FIC-1050 | Kerosene draw to C-102 | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-200 | m3/h |  |  |  | 10"-P-100-092-B1-H
FT-1050 | Flow transmitter | FIC-1050 | Kerosene draw to C-102 | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-200 | m3/h |  |  |  | 10"-P-100-092-B1-H
FV-1050 | Flow control valve | FIC-1050 | Kerosene draw to C-102 | CFU-100-PR-PID-008 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 10"-P-100-092-B1-H
LIC-1051 | Level indicating controller | LIC-1051 | C-102 bottom level | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 8"-P-100-097-B1-H
LT-1051 | Level transmitter | LIC-1051 | C-102 bottom level | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 8"-P-100-097-B1-H
FE-1052 | Flow element (orifice) | FIC-1052 | C-102 product flow element | CFU-100-PR-PID-008 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-103-A1-N
FIC-1052 | Flow indicating controller | FIC-1052 | Kerosene product | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-120 | m3/h |  |  |  | 6"-P-100-103-A1-N
FT-1052 | Flow transmitter | FIC-1052 | Kerosene product | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-120 | m3/h |  |  |  | 6"-P-100-103-A1-N
FV-1052 | Flow control valve | FIC-1052 | Kerosene product | CFU-100-PR-PID-008 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-P-100-103-A1-N
FE-1054 | Flow element (orifice) | FIC-1054 | C-102 stripping steam flow element | CFU-100-PR-PID-008 | Local | - (local / mechanical) | [5 empty] | 6"-LS-100-098-S1-H
FIC-1054 | Flow indicating controller | FIC-1054 | C-102 stripping steam | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-2000 | kg/h |  |  |  | 6"-LS-100-098-S1-H
FT-1054 | Flow transmitter | FIC-1054 | C-102 stripping steam | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-2000 | kg/h |  |  |  | 6"-LS-100-098-S1-H
FV-1054 | Flow control valve | FIC-1054 | C-102 stripping steam | CFU-100-PR-PID-008 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-LS-100-098-S1-H
FE-1060 | Flow element (orifice) | FIC-1060 | C-103 feed (draw) flow element | CFU-100-PR-PID-008 | Local | - (local / mechanical) | [5 empty] | 10"-P-100-093-B2-H
FIC-1060 | Flow indicating controller | FIC-1060 | Diesel draw to C-103 | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-250 | m3/h |  |  |  | 10"-P-100-093-B2-H
FT-1060 | Flow transmitter | FIC-1060 | Diesel draw to C-103 | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-250 | m3/h |  |  |  | 10"-P-100-093-B2-H
FV-1060 | Flow control valve | FIC-1060 | Diesel draw to C-103 | CFU-100-PR-PID-008 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 10"-P-100-093-B2-H
LIC-1061 | Level indicating controller | LIC-1061 | C-103 bottom level | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 8"-P-100-099-B2-H
LT-1061 | Level transmitter | LIC-1061 | C-103 bottom level | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 8"-P-100-099-B2-H
FE-1062 | Flow element (orifice) | FIC-1062 | C-103 product flow element | CFU-100-PR-PID-008 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-104-A1-N
FIC-1062 | Flow indicating controller | FIC-1062 | Diesel product | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-150 | m3/h |  |  |  | 6"-P-100-104-A1-N
FT-1062 | Flow transmitter | FIC-1062 | Diesel product | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-150 | m3/h |  |  |  | 6"-P-100-104-A1-N
FV-1062 | Flow control valve | FIC-1062 | Diesel product | CFU-100-PR-PID-008 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-P-100-104-A1-N
FE-1064 | Flow element (orifice) | FIC-1064 | C-103 stripping steam flow element | CFU-100-PR-PID-008 | Local | - (local / mechanical) | [5 empty] | 6"-LS-100-100-S1-H
FIC-1064 | Flow indicating controller | FIC-1064 | C-103 stripping steam | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-2500 | kg/h |  |  |  | 6"-LS-100-100-S1-H
FT-1064 | Flow transmitter | FIC-1064 | C-103 stripping steam | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-2500 | kg/h |  |  |  | 6"-LS-100-100-S1-H
FV-1064 | Flow control valve | FIC-1064 | C-103 stripping steam | CFU-100-PR-PID-008 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-LS-100-100-S1-H
FE-1070 | Flow element (orifice) | FIC-1070 | C-104 feed (draw) flow element | CFU-100-PR-PID-008 | Local | - (local / mechanical) | [5 empty] | 8"-P-100-089-B2-H
FIC-1070 | Flow indicating controller | FIC-1070 | AGO draw to C-104 | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-120 | m3/h |  |  |  | 8"-P-100-089-B2-H
FT-1070 | Flow transmitter | FIC-1070 | AGO draw to C-104 | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-120 | m3/h |  |  |  | 8"-P-100-089-B2-H
FV-1070 | Flow control valve | FIC-1070 | AGO draw to C-104 | CFU-100-PR-PID-008 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 8"-P-100-089-B2-H
LIC-1071 | Level indicating controller | LIC-1071 | C-104 bottom level | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 6"-P-100-101-B2-H
LT-1071 | Level transmitter | LIC-1071 | C-104 bottom level | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 6"-P-100-101-B2-H
FE-1072 | Flow element (orifice) | FIC-1072 | C-104 product flow element | CFU-100-PR-PID-008 | Local | - (local / mechanical) | [5 empty] | 4"-P-100-105-B1-ST
FIC-1072 | Flow indicating controller | FIC-1072 | AGO product | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-80 | m3/h |  |  |  | 4"-P-100-105-B1-ST
FT-1072 | Flow transmitter | FIC-1072 | AGO product | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-80 | m3/h |  |  |  | 4"-P-100-105-B1-ST
FV-1072 | Flow control valve | FIC-1072 | AGO product | CFU-100-PR-PID-008 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 4"-P-100-105-B1-ST
FE-1074 | Flow element (orifice) | FIC-1074 | C-104 stripping steam flow element | CFU-100-PR-PID-008 | Local | - (local / mechanical) | [5 empty] | 4"-LS-100-102-S1-H
FIC-1074 | Flow indicating controller | FIC-1074 | C-104 stripping steam | CFU-100-PR-PID-008 | DCS | Soft (DCS function block) | 0-1200 | kg/h |  |  |  | 4"-LS-100-102-S1-H
FT-1074 | Flow transmitter | FIC-1074 | C-104 stripping steam | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-1200 | kg/h |  |  |  | 4"-LS-100-102-S1-H
FV-1074 | Flow control valve | FIC-1074 | C-104 stripping steam | CFU-100-PR-PID-008 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 4"-LS-100-102-S1-H
FE-1080 | Flow element (orifice) | FI-1080 | Overflash flow element | CFU-100-PR-PID-006 | Local | - (local / mechanical) | [5 empty] | 4"-P-100-090-B2-H
FI-1080 | Flow indicator | FI-1080 | Overflash (wash-zone liquid) flow | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-100 | %
FT-1080 | Flow transmitter | FI-1080 | Overflash (wash-zone liquid) flow | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-40 | m3/h |  |  |  | 4"-P-100-090-B2-H
FE-1081 | Flow element (orifice) | FIC-1081 | C-101 stripping steam flow element | CFU-100-PR-PID-006 | Local | - (local / mechanical) | [5 empty] | 10"-LS-100-087-S1-H
FIC-1081 | Flow indicating controller | FIC-1081 | C-101 bottom stripping steam | CFU-100-PR-PID-006 | DCS | Soft (DCS function block) | 0-10000 | kg/h |  |  |  | 10"-LS-100-087-S1-H
FT-1081 | Flow transmitter | FIC-1081 | C-101 bottom stripping steam | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-10000 | kg/h |  |  |  | 10"-LS-100-087-S1-H
FV-1081 | Flow control valve | FIC-1081 | C-101 bottom stripping steam | CFU-100-PR-PID-006 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 10"-LS-100-087-S1-H
LIC-1082 | Level indicating controller | LIC-1082 | C-101 bottom level | CFU-100-PR-PID-006 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 14"-P-100-084-B2-H
LT-1082 | Level transmitter | LIC-1082 | C-101 bottom level | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 14"-P-100-084-B2-H
LT-1082B | Level transmitter | LIC-1082 | C-101 high-high bottom level -> stop P-101 / close FV-1001 | CFU-100-PR-PID-006 | SIS | 4-20 mA HART (SIS AI) | 0-100 | % |  | SIF-108 | SIL 1 | 14"-P-100-084-B2-H
LZHH-1082 | Level high-high trip function (SIS) | LIC-1082 | C-101 high-high bottom level -> stop P-101 / close FV-1001 | CFU-100-PR-PID-006 | SIS | Soft (SIS logic) | 0-100 | % |  | SIF-108 | SIL 1 | 14"-P-100-084-B2-H
FE-1083 | Flow element (orifice) | FIC-1083 | AR flow element | CFU-100-PR-PID-006 | Local | - (local / mechanical) | [5 empty] | 10"-P-100-085-B2-H
FIC-1083 | Flow indicating controller | FIC-1083 | Atm. residue to H-201 | CFU-100-PR-PID-006 | DCS | Soft (DCS function block) | 0-500 | m3/h |  |  |  | 10"-P-100-085-B2-H
FT-1083 | Flow transmitter | FIC-1083 | Atm. residue to H-201 | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-500 | m3/h |  |  |  | 10"-P-100-085-B2-H
FV-1083 | Flow control valve | FIC-1083 | Atm. residue to H-201 | CFU-100-PR-PID-006 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 10"-P-100-085-B2-H
XV-1083 | On/off shutdown valve | FIC-1083 | C-201 high-high bottom level -> trip FV-1083 / P-112 | CFU-100-PR-PID-006 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-203 | SIL 1 | 10"-P-100-085-B2-H
FIC-1090 | Flow indicating controller | FIC-1090 | Stabiliser feed (shares FT/FV-1034) | CFU-100-PR-PID-009 | DCS | Soft (DCS function block) | 0-100 | %
PIC-1091 | Pressure indicating controller | PIC-1091 | C-105 pressure (hot-vapour bypass) | CFU-100-PR-PID-010 | DCS | Soft (DCS function block) | 0-20 | barg |  |  |  | 6"-PG-100-123-C1-H
PT-1091 | Pressure transmitter | PIC-1091 | C-105 pressure (hot-vapour bypass) | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-20 | barg |  |  |  | 6"-PG-100-123-C1-H
PT-1091B | Pressure transmitter | PIC-1091 | C-105 high-high pressure -> cut reboiler steam | CFU-100-PR-PID-010 | SIS | 4-20 mA HART (SIS AI) | 0-20 | barg |  | SIF-110 | SIL 1 | 6"-PG-100-123-C1-H
PV-1091 | Pressure control valve | PIC-1091 | C-105 pressure (hot-vapour bypass) | CFU-100-PR-PID-010 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-PG-100-123-C1-H
PZHH-1091 | Pressure high-high trip function (SIS) | PIC-1091 | C-105 high-high pressure -> cut reboiler steam | CFU-100-PR-PID-010 | SIS | Soft (SIS logic) | 0-20 | barg |  | SIF-110 | SIL 1 | 6"-PG-100-123-C1-H
LIC-1092 | Level indicating controller | LIC-1092 | D-105 level | CFU-100-PR-PID-010 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 6"-P-100-126-C1-N
LT-1092 | Level transmitter | LIC-1092 | D-105 level | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 6"-P-100-126-C1-N
LT-1092B | Level transmitter | LIC-1092 | D-105 low-low level -> close LPG product XV (gas blow-by to LPG treating) | CFU-100-PR-PID-010 | SIS | 4-20 mA HART (SIS AI) | 0-100 | % |  | SIF-109 | SIL 1 | 6"-P-100-126-C1-N
LZLL-1092 | Level low-low trip function (SIS) | LIC-1092 | D-105 low-low level -> close LPG product XV (gas blow-by to LPG treating) | CFU-100-PR-PID-010 | SIS | Soft (SIS logic) | 0-100 | % |  | SIF-109 | SIL 1 | 6"-P-100-126-C1-N
FE-1093 | Flow element (orifice) | FIC-1093 | LPG product flow element | CFU-100-PR-PID-010 | Local | - (local / mechanical) | [5 empty] | 2"-P-100-128-C1-N
FIC-1093 | Flow indicating controller | FIC-1093 | LPG product | CFU-100-PR-PID-010 | DCS | Soft (DCS function block) | 0-20 | m3/h |  |  |  | 2"-P-100-128-C1-N
FT-1093 | Flow transmitter | FIC-1093 | LPG product | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-20 | m3/h |  |  |  | 2"-P-100-128-C1-N
FV-1093 | Flow control valve | FIC-1093 | LPG product | CFU-100-PR-PID-010 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 2"-P-100-128-C1-N
XV-1093 | On/off shutdown valve | FIC-1093 | D-105 low-low level -> close LPG product XV (gas blow-by to LPG treating) | CFU-100-PR-PID-010 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-109 | SIL 1 | 2"-P-100-128-C1-N
FE-1094 | Flow element (orifice) | FIC-1094 | Stabiliser reflux flow element | CFU-100-PR-PID-010 | Local | - (local / mechanical) | [5 empty] | 3"-P-100-127-C1-N
FIC-1094 | Flow indicating controller | FIC-1094 | C-105 reflux | CFU-100-PR-PID-010 | DCS | Soft (DCS function block) | 0-40 | m3/h |  |  |  | 3"-P-100-127-C1-N
FT-1094 | Flow transmitter | FIC-1094 | C-105 reflux | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-40 | m3/h |  |  |  | 3"-P-100-127-C1-N
FV-1094 | Flow control valve | FIC-1094 | C-105 reflux | CFU-100-PR-PID-010 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 3"-P-100-127-C1-N
TIC-1095 | Temperature indicating controller | TIC-1095 | C-105 sensitive tray temperature (RVP) | CFU-100-PR-PID-010 | DCS | Soft (DCS function block) | 0-300 | C |  |  |  | 6"-P-100-133-C1-H
TT-1095 | Temperature transmitter | TIC-1095 | C-105 sensitive tray temperature (RVP) | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-300 | C |  |  |  | 6"-P-100-133-C1-H
FE-1096 | Flow element (orifice) | FIC-1096 | HP steam to E-116 flow element | CFU-100-PR-PID-010 | Local | - (local / mechanical) | [5 empty] | 6"-HS-100-135-S2-H
FIC-1096 | Flow indicating controller | FIC-1096 | HP steam to E-116 | CFU-100-PR-PID-010 | DCS | Soft (DCS function block) | 0-30000 | kg/h |  |  |  | 6"-HS-100-135-S2-H
FT-1096 | Flow transmitter | FIC-1096 | HP steam to E-116 | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-30000 | kg/h |  |  |  | 6"-HS-100-135-S2-H
FV-1096 | Flow control valve | FIC-1096 | HP steam to E-116 | CFU-100-PR-PID-010 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-HS-100-135-S2-H
XV-1096 | On/off shutdown valve | FIC-1096 | C-105 high-high pressure -> cut reboiler steam | CFU-100-PR-PID-010 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-110 | SIL 1 | 6"-HS-100-135-S2-H
LIC-1097 | Level indicating controller | LIC-1097 | C-105 bottom level | CFU-100-PR-PID-010 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 6"-P-100-134-C1-H
LT-1097 | Level transmitter | LIC-1097 | C-105 bottom level | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 6"-P-100-134-C1-H
LV-1097 | Level control valve | LIC-1097 | C-105 bottom level | CFU-100-PR-PID-010 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-P-100-134-C1-H
LIC-1098 | Level indicating controller | LIC-1098 | E-116 condensate pot level | CFU-100-PR-PID-010 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 8"-CD-100-137-S1-P
LT-1098 | Level transmitter | LIC-1098 | E-116 condensate pot level | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 8"-CD-100-137-S1-P
LV-1098 | Level control valve | LIC-1098 | E-116 condensate pot level | CFU-100-PR-PID-010 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 8"-CD-100-137-S1-P
PIC-1100 | Pressure indicating controller | PIC-1100 | C-106 / D-106 pressure | CFU-100-PR-PID-011 | DCS | Soft (DCS function block) | 0-4 | barg |  |  |  | 20"-PG-100-141-A1-H
PT-1100 | Pressure transmitter | PIC-1100 | C-106 / D-106 pressure | CFU-100-PR-PID-011 | DCS | 4-20 mA HART | 0-4 | barg |  |  |  | 20"-PG-100-141-A1-H
PV-1100 | Pressure control valve | PIC-1100 | C-106 / D-106 pressure | CFU-100-PR-PID-011 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 20"-PG-100-141-A1-H
LIC-1101 | Level indicating controller | LIC-1101 | D-106 level | CFU-100-PR-PID-011 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 8"-P-100-144-A1-N
LT-1101 | Level transmitter | LIC-1101 | D-106 level | CFU-100-PR-PID-011 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 8"-P-100-144-A1-N
FE-1102 | Flow element (orifice) | FIC-1102 | Light naphtha flow element | CFU-100-PR-PID-011 | Local | - (local / mechanical) | [5 empty] | 3"-P-100-146-A1-N
FIC-1102 | Flow indicating controller | FIC-1102 | Light naphtha product | CFU-100-PR-PID-011 | DCS | Soft (DCS function block) | 0-60 | m3/h |  |  |  | 3"-P-100-146-A1-N
FT-1102 | Flow transmitter | FIC-1102 | Light naphtha product | CFU-100-PR-PID-011 | DCS | 4-20 mA HART | 0-60 | m3/h |  |  |  | 3"-P-100-146-A1-N
FV-1102 | Flow control valve | FIC-1102 | Light naphtha product | CFU-100-PR-PID-011 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 3"-P-100-146-A1-N
FE-1103 | Flow element (orifice) | FIC-1103 | Splitter reflux flow element | CFU-100-PR-PID-011 | Local | - (local / mechanical) | [5 empty] | 4"-P-100-145-A1-N
FIC-1103 | Flow indicating controller | FIC-1103 | C-106 reflux | CFU-100-PR-PID-011 | DCS | Soft (DCS function block) | 0-120 | m3/h |  |  |  | 4"-P-100-145-A1-N
FT-1103 | Flow transmitter | FIC-1103 | C-106 reflux | CFU-100-PR-PID-011 | DCS | 4-20 mA HART | 0-120 | m3/h |  |  |  | 4"-P-100-145-A1-N
FV-1103 | Flow control valve | FIC-1103 | C-106 reflux | CFU-100-PR-PID-011 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 4"-P-100-145-A1-N
TIC-1104 | Temperature indicating controller | TIC-1104 | C-106 sensitive tray temperature | CFU-100-PR-PID-011 | DCS | Soft (DCS function block) | 0-250 | C |  |  |  | 20"-P-100-148-B1-H
TT-1104 | Temperature transmitter | TIC-1104 | C-106 sensitive tray temperature | CFU-100-PR-PID-011 | DCS | 4-20 mA HART | 0-250 | C |  |  |  | 20"-P-100-148-B1-H
FE-1105 | Flow element (orifice) | FIC-1105 | MP steam to E-117 flow element | CFU-100-PR-PID-011 | Local | - (local / mechanical) | [5 empty] | 8"-MS-100-152-S3-H
FIC-1105 | Flow indicating controller | FIC-1105 | MP steam to E-117 | CFU-100-PR-PID-011 | DCS | Soft (DCS function block) | 0-20000 | kg/h |  |  |  | 8"-MS-100-152-S3-H
FT-1105 | Flow transmitter | FIC-1105 | MP steam to E-117 | CFU-100-PR-PID-011 | DCS | 4-20 mA HART | 0-20000 | kg/h |  |  |  | 8"-MS-100-152-S3-H
FV-1105 | Flow control valve | FIC-1105 | MP steam to E-117 | CFU-100-PR-PID-011 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 8"-MS-100-152-S3-H
LIC-1106 | Level indicating controller | LIC-1106 | C-106 bottom level | CFU-100-PR-PID-011 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 8"-P-100-149-A1-H
LT-1106 | Level transmitter | LIC-1106 | C-106 bottom level | CFU-100-PR-PID-011 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 8"-P-100-149-A1-H
FE-1107 | Flow element (orifice) | FIC-1107 | Heavy naphtha flow element | CFU-100-PR-PID-011 | Local | - (local / mechanical) | [5 empty] | 6"-P-100-151-A1-N
FIC-1107 | Flow indicating controller | FIC-1107 | Heavy naphtha product | CFU-100-PR-PID-011 | DCS | Soft (DCS function block) | 0-150 | m3/h |  |  |  | 6"-P-100-151-A1-N
FT-1107 | Flow transmitter | FIC-1107 | Heavy naphtha product | CFU-100-PR-PID-011 | DCS | 4-20 mA HART | 0-150 | m3/h |  |  |  | 6"-P-100-151-A1-N
FV-1107 | Flow control valve | FIC-1107 | Heavy naphtha product | CFU-100-PR-PID-011 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-P-100-151-A1-N
LIC-1110 | Level indicating controller | LIC-1110 | E-113 steam-generator level | CFU-100-PR-PID-003 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 2"-BFW-100-055-C1-H
LT-1110 | Level transmitter | LIC-1110 | E-113 steam-generator level | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 2"-BFW-100-055-C1-H
LV-1110 | Level control valve | LIC-1110 | E-113 steam-generator level | CFU-100-PR-PID-003 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 2"-BFW-100-055-C1-H
PIC-1111 | Pressure indicating controller | PIC-1111 | E-113 MP steam pressure | CFU-100-PR-PID-003 | DCS | Soft (DCS function block) | 0-20 | barg |  |  |  | 6"-MS-100-056-S3-H
PT-1111 | Pressure transmitter | PIC-1111 | E-113 MP steam pressure | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-20 | barg |  |  |  | 6"-MS-100-056-S3-H
PV-1111 | Pressure control valve | PIC-1111 | E-113 MP steam pressure | CFU-100-PR-PID-003 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-MS-100-056-S3-H
BY-1121 | Burner / flame BY | BY-1121 | Fire confirmation from F&G (P-112 area) | CFU-100-PR-PID-006 | F&G | DI 24 VDC |  |  |  | SIF-204 | SIL 1
EIV-1121 | Emergency isolation valve (ROSOV) | EIV-1121 | Pump P-112/P-204 hot-pump emergency isolation (fire) | CFU-100-PR-PID-006 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-204 | SIL 1
HS-1121 | Hand switch | HS-1121 | EIV-1121 manual close (CCR + field) | CFU-100-PR-PID-006 | SIS | DI 24 VDC |  |  |  | SIF-204 | SIL 1
PI-1200 | Pressure gauge | PI-1200 | P-101A discharge pressure | CFU-100-PR-PID-001 | Local | - (local / mechanical) | 0-40 | barg |  |  |  | 12"-P-100-002-B1-N
PI-1201 | Pressure gauge | PI-1201 | P-101B discharge pressure | CFU-100-PR-PID-001 | Local | - (local / mechanical) | 0-40 | barg |  |  |  | 12"-P-100-002-B1-N
TI-1202 | Temperature indicator | TI-1202 | Crude E-101 outlet | CFU-100-PR-PID-001 | DCS | 4-20 mA HART | 0-120 | C |  |  |  | 12"-P-100-005-B1-N
TI-1203 | Temperature indicator | TI-1203 | Crude E-102 outlet | CFU-100-PR-PID-001 | DCS | 4-20 mA HART | 0-150 | C |  |  |  | 12"-P-100-006-B1-H
TI-1204 | Temperature indicator | TI-1204 | Crude E-103 outlet | CFU-100-PR-PID-001 | DCS | 4-20 mA HART | 0-200 | C |  |  |  | 12"-P-100-007-B1-H
TI-1205 | Temperature indicator | TI-1205 | Crude E-104 outlet | CFU-100-PR-PID-001 | DCS | 4-20 mA HART | 0-200 | C |  |  |  | 12"-P-100-008-B1-H
TI-1206 | Temperature indicator | TI-1206 | Crude E-105 outlet | CFU-100-PR-PID-001 | DCS | 4-20 mA HART | 0-200 | C |  |  |  | 12"-P-100-009-B1-H
PI-1207 | Pressure gauge | PI-1207 | P-102A discharge pressure | CFU-100-PR-PID-002 | Local | - (local / mechanical) | 0-50 | barg |  |  |  | 12"-P-100-023-B1-H
PI-1208 | Pressure gauge | PI-1208 | P-102B discharge pressure | CFU-100-PR-PID-002 | Local | - (local / mechanical) | 0-50 | barg |  |  |  | 12"-P-100-023-B1-H
TI-1209 | Temperature indicator | TI-1209 | Desalted crude temperature | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-200 | C |  |  |  | 20"-P-100-022-B1-H
PI-1210 | Pressure gauge | PI-1210 | D-101A pressure | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-5 | barg
PI-1211 | Pressure gauge | PI-1211 | D-101B pressure | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-5 | barg
TI-1212 | Temperature indicator | TI-1212 | Brine to WWT temperature | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-200 | C |  |  |  | 3"-WW-100-032-A3-P
PI-1213 | Pressure gauge | PI-1213 | P-114A discharge pressure | CFU-100-PR-PID-002 | Local | - (local / mechanical) | 0-25 | barg |  |  |  | 3"-WW-100-027-A3-N
PI-1214 | Pressure gauge | PI-1214 | P-114B discharge pressure | CFU-100-PR-PID-002 | Local | - (local / mechanical) | 0-25 | barg |  |  |  | 3"-WW-100-027-A3-N
TI-1215 | Temperature indicator | TI-1215 | Wash water to desalter temperature | CFU-100-PR-PID-002 | DCS | 4-20 mA HART | 0-200 | C |  |  |  | 3"-WW-100-028-A3-P
PI-1216 | Pressure gauge | PI-1216 | P-118 discharge pressure | CFU-100-PR-PID-002 | Local | - (local / mechanical) | 0-30 | barg |  |  |  | 3"-WW-100-034-A3-P
TI-1217 | Temperature indicator | TI-1217 | Crude E-106 outlet | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-250 | C |  |  |  | 12"-P-100-037-B1-H
TI-1218 | Temperature indicator | TI-1218 | Crude E-107 outlet | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-250 | C |  |  |  | 14"-P-100-038-B1-H
TI-1219 | Temperature indicator | TI-1219 | Crude E-108 outlet | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-400 | C |  |  |  | 14"-P-100-039-B1-H
TI-1220 | Temperature indicator | TI-1220 | Crude E-109 outlet | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-400 | C |  |  |  | 14"-P-100-040-B1-H
TI-1221 | Temperature indicator | TI-1221 | Crude E-110 outlet | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-400 | C |  |  |  | 14"-P-100-041-C1-H
TI-1222 | Temperature indicator | TI-1222 | Crude E-111 outlet | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-400 | C |  |  |  | 18"-P-100-042-B2-H
TI-1223 | Temperature indicator | TI-1223 | CIT - crude to H-101 | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-400 | C |  |  |  | 18"-P-100-042-B2-H
PI-1224 | Pressure gauge | PI-1224 | Crude to H-101 pressure | CFU-100-PR-PID-003 | DCS | 4-20 mA HART | 0-30 | barg |  |  |  | 18"-P-100-042-B2-H
LG-1225 | Level gauge | LG-1225 | E-113 level gauge | CFU-100-PR-PID-003 | Local | - (local / mechanical) | 0-100 | %
TI-1226 | Temperature indicator | TI-1226 | H-101 inlet temperature (CIT) | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-400 | C |  |  |  | 18"-P-100-042-B2-H
PI-1227 | Pressure gauge | PI-1227 | Stripping steam pressure | CFU-100-PR-PID-004 | DCS | 4-20 mA HART | 0-6 | barg |  |  |  | 12"-LS-100-077-S1-H
TI-1228 | Temperature indicator | TI-1228 | H-101 flue gas temperature (bridgewall) | CFU-100-PR-PID-005 | DCS | 4-20 mA HART | 0-400 | C
PI-1229 | Pressure gauge | PI-1229 | H-101 fuel gas supply pressure | CFU-100-PR-PID-005 | Local | - (local / mechanical) | 0-6 | barg |  |  |  | 8"-FG-100-079-A1-N
XV-1230 | On/off shutdown valve | XV-1230 | H-101 FG double block & bleed vent | CFU-100-PR-PID-005 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FO | SIF-101 | SIL 2
ZSC-1231 | Limit switch closed | ZSC-1231 | Closed limit switch on XV-1021 | CFU-100-PR-PID-005 | SIS | DI 24 VDC
ZSC-1232 | Limit switch closed | ZSC-1232 | Closed limit switch on XV-1022 | CFU-100-PR-PID-005 | SIS | DI 24 VDC
PCV-1233 | Self-acting pressure regulator | PCV-1233 | H-101 pilot gas self-acting regulator | CFU-100-PR-PID-005 | Local | - (local / mechanical)
TI-1234 | Temperature indicator | TI-1234 | C-101 flash zone feed temperature (COT) | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 28"-P-100-075-B3-H
TI-1235 | Temperature indicator | TI-1235 | AGO draw temperature | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 8"-P-100-089-B2-H
PT-1236 | Pressure transmitter | PT-1236 | C-101 flash zone pressure | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-5 | barg
PDI-1237 | Differential pressure indicator | PDI-1237 | C-101 column dP (top - flash zone) | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-2.5 | bar
PI-1238 | Pressure gauge | PI-1238 | P-112A discharge pressure | CFU-100-PR-PID-006 | Local | - (local / mechanical) | 0-30 | barg |  |  |  | 10"-P-100-085-B2-H
PI-1239 | Pressure gauge | PI-1239 | P-112B discharge pressure | CFU-100-PR-PID-006 | Local | - (local / mechanical) | 0-30 | barg |  |  |  | 10"-P-100-085-B2-H
TI-1240 | Temperature indicator | TI-1240 | AR to H-201 temperature | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 10"-P-100-085-B2-H
LG-1241 | Level gauge | LG-1241 | C-101 bottom level gauge | CFU-100-PR-PID-006 | Local | - (local / mechanical) | 0-100 | %
TI-1242 | Temperature indicator | TI-1242 | C-101 bottoms temperature | CFU-100-PR-PID-006 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 14"-P-100-084-B2-H
PT-1243 | Pressure transmitter | PT-1243 | C-101 top pressure | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-5 | barg
TI-1244 | Temperature indicator | TI-1244 | Kero draw temperature | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-300 | C |  |  |  | 10"-P-100-092-B1-H
TI-1245 | Temperature indicator | TI-1245 | Dsl draw temperature | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-400 | C |  |  |  | 10"-P-100-093-B2-H
PI-1246 | Pressure gauge | PI-1246 | P-106A discharge pressure | CFU-100-PR-PID-007 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 8"-P-100-014-A1-H
PI-1247 | Pressure gauge | PI-1247 | P-106B discharge pressure | CFU-100-PR-PID-007 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 8"-P-100-014-A1-H
TI-1248 | Temperature indicator | TI-1248 | TPA draw temperature | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-250 | C |  |  |  | 12"-P-100-013-A1-H
PI-1249 | Pressure gauge | PI-1249 | P-107A discharge pressure | CFU-100-PR-PID-007 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 10"-P-100-044-B1-H
PI-1250 | Pressure gauge | PI-1250 | P-107B discharge pressure | CFU-100-PR-PID-007 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 10"-P-100-044-B1-H
TI-1251 | Temperature indicator | TI-1251 | MPA draw temperature | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-400 | C |  |  |  | 14"-P-100-043-B1-H
PI-1252 | Pressure gauge | PI-1252 | P-108A discharge pressure | CFU-100-PR-PID-007 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 8"-P-100-051-B2-H
PI-1253 | Pressure gauge | PI-1253 | P-108B discharge pressure | CFU-100-PR-PID-007 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 8"-P-100-051-B2-H
TI-1254 | Temperature indicator | TI-1254 | BPA draw temperature | CFU-100-PR-PID-007 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 12"-P-100-050-B2-H
PI-1255 | Pressure gauge | PI-1255 | C-102 pressure | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-5 | barg
PI-1256 | Pressure gauge | PI-1256 | P-109A discharge pressure | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-20 | barg |  |  |  | 6"-P-100-017-B1-H
PI-1257 | Pressure gauge | PI-1257 | P-109B discharge pressure | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-20 | barg |  |  |  | 6"-P-100-017-B1-H
LG-1258 | Level gauge | LG-1258 | C-102 level gauge | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-100 | %
TI-1259 | Temperature indicator | TI-1259 | C-102 product rundown temperature | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-100 | C |  |  |  | 6"-P-100-103-A1-N
PI-1260 | Pressure gauge | PI-1260 | C-103 pressure | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-5 | barg
PI-1261 | Pressure gauge | PI-1261 | P-110A discharge pressure | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-20 | barg |  |  |  | 6"-P-100-047-B2-H
PI-1262 | Pressure gauge | PI-1262 | P-110B discharge pressure | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-20 | barg |  |  |  | 6"-P-100-047-B2-H
LG-1263 | Level gauge | LG-1263 | C-103 level gauge | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-100 | %
TI-1264 | Temperature indicator | TI-1264 | C-103 product rundown temperature | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-120 | C |  |  |  | 6"-P-100-104-A1-N
PI-1265 | Pressure gauge | PI-1265 | C-104 pressure | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-5 | barg
PI-1266 | Pressure gauge | PI-1266 | P-111A discharge pressure | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-20 | barg |  |  |  | 4"-P-100-048-B2-H
PI-1267 | Pressure gauge | PI-1267 | P-111B discharge pressure | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-20 | barg |  |  |  | 4"-P-100-048-B2-H
LG-1268 | Level gauge | LG-1268 | C-104 level gauge | CFU-100-PR-PID-008 | Local | - (local / mechanical) | 0-100 | %
TI-1269 | Temperature indicator | TI-1269 | C-104 product rundown temperature | CFU-100-PR-PID-008 | DCS | 4-20 mA HART | 0-120 | C |  |  |  | 4"-P-100-105-B1-ST
TI-1270 | Temperature indicator | TI-1270 | A-101 outlet temperature | CFU-100-PR-PID-009 | DCS | 4-20 mA HART | 0-120 | C |  |  |  | 16"-PG-100-108-A2-N
TSV-1271 | Thermal safety valve | TSV-1271 | Thermal relief, CW sides E-115, E-202..E-204 (TSV-typ, D orifice, 3/4" x 1") | CFU-100-PR-PID-009 | Local | - (local / mechanical) | Set 7.0 | barg |  |  |  |  | TSV-typ
LG-1272 | Level gauge | LG-1272 | D-102 hydrocarbon level gauge | CFU-100-PR-PID-009 | Local | - (local / mechanical) | 0-100 | %
PI-1273 | Pressure gauge | PI-1273 | D-102 pressure | CFU-100-PR-PID-009 | Local | - (local / mechanical) | 0-5 | barg
TI-1274 | Temperature indicator | TI-1274 | D-102 temperature | CFU-100-PR-PID-009 | DCS | 4-20 mA HART | 0-400 | C
PI-1275 | Pressure gauge | PI-1275 | P-105A discharge pressure | CFU-100-PR-PID-009 | Local | - (local / mechanical) | 0-8 | barg |  |  |  | 2"-SW-100-115-A2-N
PI-1276 | Pressure gauge | PI-1276 | P-105B discharge pressure | CFU-100-PR-PID-009 | Local | - (local / mechanical) | 0-8 | barg |  |  |  | 2"-SW-100-115-A2-N
PI-1277 | Pressure gauge | PI-1277 | P-103A discharge pressure | CFU-100-PR-PID-009 | Local | - (local / mechanical) | 0-12 | barg |  |  |  | 6"-P-100-111-A1-N
PI-1278 | Pressure gauge | PI-1278 | P-103B discharge pressure | CFU-100-PR-PID-009 | Local | - (local / mechanical) | 0-12 | barg |  |  |  | 6"-P-100-111-A1-N
PI-1279 | Pressure gauge | PI-1279 | P-104A discharge pressure | CFU-100-PR-PID-009 | Local | - (local / mechanical) | 0-25 | barg |  |  |  | 6"-P-100-113-B1-N
PI-1280 | Pressure gauge | PI-1280 | P-104B discharge pressure | CFU-100-PR-PID-009 | Local | - (local / mechanical) | 0-25 | barg |  |  |  | 6"-P-100-113-B1-N
TI-1281 | Temperature indicator | TI-1281 | Stabiliser feed temperature | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-150 | C |  |  |  | 6"-P-100-122-C1-H
LG-1282 | Level gauge | LG-1282 | D-105 level gauge | CFU-100-PR-PID-010 | Local | - (local / mechanical) | 0-100 | %
PI-1283 | Pressure gauge | PI-1283 | P-115A discharge pressure | CFU-100-PR-PID-010 | Local | - (local / mechanical) | 0-25 | barg |  |  |  | 3"-P-100-127-C1-N
PI-1284 | Pressure gauge | PI-1284 | P-115B discharge pressure | CFU-100-PR-PID-010 | Local | - (local / mechanical) | 0-25 | barg |  |  |  | 3"-P-100-127-C1-N
GD-1285 | Gas detector | GD-1285 | Flammable gas detector, LPG pump area P-115 (1) | CFU-100-PR-PID-010 | F&G | 4-20 mA (F&G) | 0-100 | % LEL
GD-1286 | Gas detector | GD-1286 | Flammable gas detector, LPG pump area P-115 (2) | CFU-100-PR-PID-010 | F&G | 4-20 mA (F&G) | 0-100 | % LEL
PDI-1287 | Differential pressure indicator | PDI-1287 | C-105 column dP | CFU-100-PR-PID-010 | DCS | 4-20 mA HART | 0-2.5 | bar
PI-1288 | Pressure gauge | PI-1288 | P-116A discharge pressure | CFU-100-PR-PID-011 | Local | - (local / mechanical) | 0-8 | barg |  |  |  | 4"-P-100-145-A1-N
PI-1289 | Pressure gauge | PI-1289 | P-116B discharge pressure | CFU-100-PR-PID-011 | Local | - (local / mechanical) | 0-8 | barg |  |  |  | 4"-P-100-145-A1-N
PI-1291 | Pressure gauge | PI-1291 | P-117A discharge pressure | CFU-100-PR-PID-011 | Local | - (local / mechanical) | 0-12 | barg |  |  |  | 6"-P-100-150-A1-H
PI-1292 | Pressure gauge | PI-1292 | P-117B discharge pressure | CFU-100-PR-PID-011 | Local | - (local / mechanical) | 0-12 | barg |  |  |  | 6"-P-100-150-A1-H
TI-1293 | Temperature indicator | TI-1293 | C-106 bottoms temperature | CFU-100-PR-PID-011 | DCS | 4-20 mA HART | 0-250 | C |  |  |  | 8"-P-100-149-A1-H
FE-2001 | Flow element (orifice) | FIC-2001 | H-201 pass 1 flow element | CFU-200-PR-PID-012 | Local | - (local / mechanical) | [5 empty] | 6"-P-200-009-B2-H
FIC-2001 | Flow indicating controller | FIC-2001 | H-201 pass 1 flow | CFU-200-PR-PID-012 | DCS | Soft (DCS function block) | 0-120 | m3/h |  |  |  | 6"-P-200-009-B2-H
FT-2001 | Flow transmitter | FIC-2001 | H-201 pass 1 flow | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-120 | m3/h |  |  |  | 6"-P-200-009-B2-H
FT-2001A | Flow transmitter | FIC-2001 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-009-B2-H
FT-2001B | Flow transmitter | FIC-2001 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-009-B2-H
FT-2001C | Flow transmitter | FIC-2001 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-009-B2-H
FV-2001 | Flow control valve | FIC-2001 | H-201 pass 1 flow | CFU-200-PR-PID-012 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-200-009-B2-H
FZLL-2001 | Flow low-low trip function (SIS) | FIC-2001 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | Soft (SIS logic) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-009-B2-H
PSV-2001 | Pressure safety valve | PSV-2001 |  | CFU-200-PR-PID-013 | Local | - (local / mechanical) | Set 3.5 | barg
FE-2002 | Flow element (orifice) | FIC-2002 | H-201 pass 2 flow element | CFU-200-PR-PID-012 | Local | - (local / mechanical) | [5 empty] | 6"-P-200-010-B2-H
FIC-2002 | Flow indicating controller | FIC-2002 | H-201 pass 2 flow | CFU-200-PR-PID-012 | DCS | Soft (DCS function block) | 0-120 | m3/h |  |  |  | 6"-P-200-010-B2-H
FT-2002 | Flow transmitter | FIC-2002 | H-201 pass 2 flow | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-120 | m3/h |  |  |  | 6"-P-200-010-B2-H
FT-2002A | Flow transmitter | FIC-2002 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-010-B2-H
FT-2002B | Flow transmitter | FIC-2002 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-010-B2-H
FT-2002C | Flow transmitter | FIC-2002 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-010-B2-H
FV-2002 | Flow control valve | FIC-2002 | H-201 pass 2 flow | CFU-200-PR-PID-012 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-200-010-B2-H
FZLL-2002 | Flow low-low trip function (SIS) | FIC-2002 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | Soft (SIS logic) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-010-B2-H
PSV-2002 | Pressure safety valve | PSV-2002 |  | CFU-200-PR-PID-015 | Local | - (local / mechanical) | Set 3.5 | barg
FE-2003 | Flow element (orifice) | FIC-2003 | H-201 pass 3 flow element | CFU-200-PR-PID-012 | Local | - (local / mechanical) | [5 empty] | 6"-P-200-011-B2-H
FIC-2003 | Flow indicating controller | FIC-2003 | H-201 pass 3 flow | CFU-200-PR-PID-012 | DCS | Soft (DCS function block) | 0-120 | m3/h |  |  |  | 6"-P-200-011-B2-H
FT-2003 | Flow transmitter | FIC-2003 | H-201 pass 3 flow | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-120 | m3/h |  |  |  | 6"-P-200-011-B2-H
FT-2003A | Flow transmitter | FIC-2003 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-011-B2-H
FT-2003B | Flow transmitter | FIC-2003 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-011-B2-H
FT-2003C | Flow transmitter | FIC-2003 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-011-B2-H
FV-2003 | Flow control valve | FIC-2003 | H-201 pass 3 flow | CFU-200-PR-PID-012 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-200-011-B2-H
FZLL-2003 | Flow low-low trip function (SIS) | FIC-2003 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | Soft (SIS logic) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-011-B2-H
PSV-2003 | Pressure safety valve | PSV-2003 |  | CFU-200-PR-PID-014 | Local | - (local / mechanical) | Set 5.0 | barg
FE-2004 | Flow element (orifice) | FIC-2004 | H-201 pass 4 flow element | CFU-200-PR-PID-012 | Local | - (local / mechanical) | [5 empty] | 6"-P-200-012-B2-H
FIC-2004 | Flow indicating controller | FIC-2004 | H-201 pass 4 flow | CFU-200-PR-PID-012 | DCS | Soft (DCS function block) | 0-120 | m3/h |  |  |  | 6"-P-200-012-B2-H
FT-2004 | Flow transmitter | FIC-2004 | H-201 pass 4 flow | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-120 | m3/h |  |  |  | 6"-P-200-012-B2-H
FT-2004A | Flow transmitter | FIC-2004 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-012-B2-H
FT-2004B | Flow transmitter | FIC-2004 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-012-B2-H
FT-2004C | Flow transmitter | FIC-2004 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-012-B2-H
FV-2004 | Flow control valve | FIC-2004 | H-201 pass 4 flow | CFU-200-PR-PID-012 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 6"-P-200-012-B2-H
FZLL-2004 | Flow low-low trip function (SIS) | FIC-2004 | H-201 low-low pass flow -> trip fuel | CFU-200-PR-PID-012 | SIS | Soft (SIS logic) | 0-120 | m3/h |  | SIF-201 | SIL 2 | 6"-P-200-012-B2-H
TIC-2005 | Temperature indicating controller | TIC-2005 | H-201 COT | CFU-200-PR-PID-012 | DCS | Soft (DCS function block) | 0-600 | C |  |  |  | 54"-P-200-017-B3-H
TT-2005 | Temperature transmitter | TIC-2005 | H-201 COT | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-600 | C |  |  |  | 54"-P-200-017-B3-H
PIC-2006 | Pressure indicating controller | PIC-2006 | H-201 fuel gas pressure | CFU-200-PR-PID-012 | DCS | Soft (DCS function block) | 0-6 | barg |  |  |  | 4"-FG-200-019-A1-N
PT-2006 | Pressure transmitter | PIC-2006 | H-201 fuel gas pressure | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-6 | barg |  |  |  | 4"-FG-200-019-A1-N
PV-2006 | Pressure control valve | PIC-2006 | H-201 fuel gas pressure | CFU-200-PR-PID-012 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 4"-FG-200-019-A1-N
XV-2006A | On/off shutdown valve | PIC-2006 | H-201 fuel gas SSOV | CFU-200-PR-PID-012 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-201 | SIL 2 | 4"-FG-200-019-A1-N
XV-2006B | On/off shutdown valve | PIC-2006 | H-201 fuel gas SSOV | CFU-200-PR-PID-012 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-201 | SIL 2 | 4"-FG-200-019-A1-N
FE-2007 | Flow element (orifice) | FIC-2007 | H-201 coil steam flow element | CFU-200-PR-PID-012 | Local | - (local / mechanical) | [5 empty] | 3"-MS-200-018-S3-H
FIC-2007 | Flow indicating controller | FIC-2007 | H-201 coil (velocity) steam | CFU-200-PR-PID-012 | DCS | Soft (DCS function block) | 0-1500 | kg/h |  |  |  | 3"-MS-200-018-S3-H
FT-2007 | Flow transmitter | FIC-2007 | H-201 coil (velocity) steam | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-1500 | kg/h |  |  |  | 3"-MS-200-018-S3-H
FV-2007 | Flow control valve | FIC-2007 | H-201 coil (velocity) steam | CFU-200-PR-PID-012 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 3"-MS-200-018-S3-H
AIC-2008 | Analyser indicating controller | AIC-2008 | H-201 flue gas O2 | CFU-200-PR-PID-012 | DCS | Soft (DCS function block) | 0-10 | vol% O2
AT-2008 | Analyser transmitter | AIC-2008 | H-201 flue gas O2 analyser | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-10 | vol% O2
AV-2008 | Analyser control element (damper/vane) | AIC-2008 | H-201 stack damper actuator (AIC-2008) | CFU-200-PR-PID-012 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO
BS-2008 | Flame scanner | AIC-2008 | H-201 flame scanners (1 per burner) | CFU-200-PR-PID-012 | DCS | DI 24 VDC | Flame ON/OFF | -
BZLL-2008 | Flame failure trip function (SIS) | AIC-2008 | H-201 flame failure | CFU-200-PR-PID-012 | SIS | Soft (SIS logic) | Flame ON/OFF | - |  | SIF-202 | SIL 1
PT-2009A | Pressure transmitter | PT-2009A | H-201 low-low FG pressure / flame failure -> trip | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-5 | barg |  | SIF-202 | SIL 1
PT-2009B | Pressure transmitter | PT-2009B | H-201 low-low FG pressure / flame failure -> trip | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-5 | barg |  | SIF-202 | SIL 1
PT-2009C | Pressure transmitter | PT-2009C | H-201 low-low FG pressure / flame failure -> trip | CFU-200-PR-PID-012 | SIS | 4-20 mA HART (SIS AI) | 0-5 | barg |  | SIF-202 | SIL 1
PZLL-2009 | Pressure low-low trip function (SIS) | PZLL-2009 | H-201 low-low FG pressure / flame failure -> trip (2oo3) | CFU-200-PR-PID-012 | SIS | Soft (SIS logic) | 0-5 | barg |  | SIF-202 | SIL 1
PIC-2010 | Pressure indicating controller | PIC-2010 | C-201 top pressure (vacuum) | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-1100 | mbar(a) |  |  |  | 48"-PG-200-024-V1-H
PT-2010 | Pressure transmitter | PIC-2010 | C-201 top pressure (vacuum) | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-1100 | mbar(a) |  |  |  | 48"-PG-200-024-V1-H
PV-2010 | Pressure control valve | PIC-2010 | C-201 top pressure (vacuum) | CFU-200-PR-PID-013, CFU-200-PR-PID-015 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 48"-PG-200-024-V1-H
FE-2011 | Flow element (orifice) | FIC-2011 | LVGO PA circulation flow element | CFU-200-PR-PID-014 | Local | - (local / mechanical) | [5 empty] | 6"-P-200-026-B1-N
FIC-2011 | Flow indicating controller | FIC-2011 | LVGO PA circulation | CFU-200-PR-PID-014 | DCS | Soft (DCS function block) | 0-150 | m3/h |  |  |  | 6"-P-200-026-B1-N
FT-2011 | Flow transmitter | FIC-2011 | LVGO PA circulation | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-150 | m3/h |  |  |  | 6"-P-200-026-B1-N
FV-2011 | Flow control valve | FIC-2011 | LVGO PA circulation | CFU-200-PR-PID-014 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-P-200-026-B1-N
TIC-2012 | Temperature indicating controller | TIC-2012 | C-201 top temperature | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-120 | C |  |  |  | 48"-PG-200-024-V1-H
TT-2012 | Temperature transmitter | TIC-2012 | C-201 top temperature | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-120 | C |  |  |  | 48"-PG-200-024-V1-H
TIC-2013 | Temperature indicating controller | TIC-2013 | LVGO PA return temperature | CFU-200-PR-PID-014 | DCS | Soft (DCS function block) | 0-120 | C |  |  |  | 6"-P-200-026-B1-N
TT-2013 | Temperature transmitter | TIC-2013 | LVGO PA return temperature | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-120 | C |  |  |  | 6"-P-200-026-B1-N
TY-2013 | Temperature relay / output signal | TIC-2013 | A-201 fan auto-variable pitch signal | CFU-200-PR-PID-014 | DCS | 4-20 mA AO | [5 empty] | 6"-P-200-026-B1-N
LIC-2014 | Level indicating controller | LIC-2014 | LVGO draw-pan level | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 10"-P-200-025-B1-H
LT-2014 | Level transmitter | LIC-2014 | LVGO draw-pan level | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 10"-P-200-025-B1-H
FE-2015 | Flow element (orifice) | FIC-2015 | LVGO product flow element | CFU-200-PR-PID-014 | Local | - (local / mechanical) | [5 empty] | 4"-P-200-039-B1-N
FIC-2015 | Flow indicating controller | FIC-2015 | LVGO product | CFU-200-PR-PID-014 | DCS | Soft (DCS function block) | 0-80 | m3/h |  |  |  | 4"-P-200-039-B1-N
FT-2015 | Flow transmitter | FIC-2015 | LVGO product | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-80 | m3/h |  |  |  | 4"-P-200-039-B1-N
FV-2015 | Flow control valve | FIC-2015 | LVGO product | CFU-200-PR-PID-014 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 4"-P-200-039-B1-N
FE-2016 | Flow element (orifice) | FIC-2016 | HVGO PA circulation flow element | CFU-200-PR-PID-014 | Local | - (local / mechanical) | [5 empty] | 8"-P-200-028-B1-H
FIC-2016 | Flow indicating controller | FIC-2016 | HVGO PA circulation | CFU-200-PR-PID-014 | DCS | Soft (DCS function block) | 0-300 | m3/h |  |  |  | 8"-P-200-028-B1-H
FT-2016 | Flow transmitter | FIC-2016 | HVGO PA circulation | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-300 | m3/h |  |  |  | 8"-P-200-028-B1-H
FV-2016 | Flow control valve | FIC-2016 | HVGO PA circulation | CFU-200-PR-PID-014 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 8"-P-200-028-B1-H
TIC-2017 | Temperature indicating controller | TIC-2017 | HVGO PA return temperature | CFU-200-PR-PID-014 | DCS | Soft (DCS function block) | 0-300 | C |  |  |  | 8"-P-200-028-B1-H
TT-2017 | Temperature transmitter | TIC-2017 | HVGO PA return temperature | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-300 | C |  |  |  | 8"-P-200-028-B1-H
TV-2017 | Temperature control valve | TIC-2017 | HVGO PA return temperature | CFU-100-PR-PID-003, CFU-200-PR-PID-014 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 8"-P-200-006-B1-H
LIC-2018 | Level indicating controller | LIC-2018 | HVGO draw-pan level | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 14"-P-200-027-B2-H
LT-2018 | Level transmitter | LIC-2018 | HVGO draw-pan level | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 14"-P-200-027-B2-H
FE-2019 | Flow element (orifice) | FIC-2019 | HVGO product flow element | CFU-200-PR-PID-014 | Local | - (local / mechanical) | [5 empty] | 6"-P-200-041-B1-ST
FIC-2019 | Flow indicating controller | FIC-2019 | HVGO product | CFU-200-PR-PID-014 | DCS | Soft (DCS function block) | 0-150 | m3/h |  |  |  | 6"-P-200-041-B1-ST
FT-2019 | Flow transmitter | FIC-2019 | HVGO product | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-150 | m3/h |  |  |  | 6"-P-200-041-B1-ST
FV-2019 | Flow control valve | FIC-2019 | HVGO product | CFU-200-PR-PID-014 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-P-200-041-B1-ST
FE-2020 | Flow element (orifice) | FIC-2020 | Wash oil flow element | CFU-200-PR-PID-013 | Local | - (local / mechanical) | [5 empty] | 2"-P-200-029-B2-H
FIC-2020 | Flow indicating controller | FIC-2020 | Wash oil to wash bed (critical, min-flow) | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-25 | m3/h |  |  |  | 2"-P-200-029-B2-H
FT-2020 | Flow transmitter | FIC-2020 | Wash oil to wash bed (critical, min-flow) | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-25 | m3/h |  |  |  | 2"-P-200-029-B2-H
FV-2020 | Flow control valve | FIC-2020 | Wash oil to wash bed (critical, min-flow) | CFU-200-PR-PID-013 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 2"-P-200-029-B2-H
LIC-2021 | Level indicating controller | LIC-2021 | Slop-wax pan level | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 3"-P-200-030-B2-H
LT-2021 | Level transmitter | LIC-2021 | Slop-wax pan level | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 3"-P-200-030-B2-H
FE-2022 | Flow element (orifice) | FIC-2022 | Slop wax product flow element | CFU-200-PR-PID-014 | Local | - (local / mechanical) | [5 empty] | 2"-P-200-031-B2-ST
FIC-2022 | Flow indicating controller | FIC-2022 | Slop wax product | CFU-200-PR-PID-014 | DCS | Soft (DCS function block) | 0-15 | m3/h |  |  |  | 2"-P-200-031-B2-ST
FT-2022 | Flow transmitter | FIC-2022 | Slop wax product | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-15 | m3/h |  |  |  | 2"-P-200-031-B2-ST
FV-2022 | Flow control valve | FIC-2022 | Slop wax product | CFU-200-PR-PID-014 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 2"-P-200-031-B2-ST
FE-2023 | Flow element (orifice) | FIC-2023 | C-201 stripping steam flow element | CFU-200-PR-PID-013 | Local | - (local / mechanical) | [5 empty] | 4"-MS-200-032-S3-H
FIC-2023 | Flow indicating controller | FIC-2023 | C-201 bottom stripping steam | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-4000 | kg/h |  |  |  | 4"-MS-200-032-S3-H
FT-2023 | Flow transmitter | FIC-2023 | C-201 bottom stripping steam | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-4000 | kg/h |  |  |  | 4"-MS-200-032-S3-H
FV-2023 | Flow control valve | FIC-2023 | C-201 bottom stripping steam | CFU-200-PR-PID-013 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 4"-MS-200-032-S3-H
LIC-2024 | Level indicating controller | LIC-2024 | C-201 bottom level | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 10"-P-200-033-B2-ST
LT-2024 | Level transmitter | LIC-2024 | C-201 bottom level | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 10"-P-200-033-B2-ST
LT-2024B | Level transmitter | LIC-2024 | C-201 high-high bottom level -> trip FV-1083 / P-112 | CFU-200-PR-PID-013 | SIS | 4-20 mA HART (SIS AI) | 0-100 | % |  | SIF-203 | SIL 1 | 10"-P-200-033-B2-ST
LZHH-2024 | Level high-high trip function (SIS) | LIC-2024 | C-201 high-high bottom level -> trip FV-1083 / P-112 | CFU-200-PR-PID-013 | SIS | Soft (SIS logic) | 0-100 | % |  | SIF-203 | SIL 1 | 10"-P-200-033-B2-ST
FE-2025 | Flow element (orifice) | FIC-2025 | Vacuum residue product flow element | CFU-200-PR-PID-014 | Local | - (local / mechanical) | [5 empty] | 6"-P-200-042-B1-ST
FIC-2025 | Flow indicating controller | FIC-2025 | Vacuum residue product | CFU-200-PR-PID-014 | DCS | Soft (DCS function block) | 0-200 | m3/h |  |  |  | 6"-P-200-042-B1-ST
FT-2025 | Flow transmitter | FIC-2025 | Vacuum residue product | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-200 | m3/h |  |  |  | 6"-P-200-042-B1-ST
FV-2025 | Flow control valve | FIC-2025 | Vacuum residue product | CFU-200-PR-PID-014 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 6"-P-200-042-B1-ST
TIC-2026 | Temperature indicating controller | TIC-2026 | C-201 bottoms temperature (coking control) | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-500 | C |  |  |  | 10"-P-200-033-B2-ST
TT-2026 | Temperature transmitter | TIC-2026 | C-201 bottoms temperature (coking control) | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 10"-P-200-033-B2-ST
FE-2027 | Flow element (orifice) | FIC-2027 | VR quench flow element | CFU-200-PR-PID-013 | Local | - (local / mechanical) | [5 empty] | 3"-P-200-034-B1-ST
FIC-2027 | Flow indicating controller | FIC-2027 | VR quench flow | CFU-200-PR-PID-013 | DCS | Soft (DCS function block) | 0-40 | m3/h |  |  |  | 3"-P-200-034-B1-ST
FT-2027 | Flow transmitter | FIC-2027 | VR quench flow | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-40 | m3/h |  |  |  | 3"-P-200-034-B1-ST
FV-2027 | Flow control valve | FIC-2027 | VR quench flow | CFU-200-PR-PID-013 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 3"-P-200-034-B1-ST
LIC-2028 | Level indicating controller | LIC-2028 | D-201 hotwell water level | CFU-200-PR-PID-015 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 2"-SW-200-061-A2-N
LT-2028 | Level transmitter | LIC-2028 | D-201 hotwell water level | CFU-200-PR-PID-015 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 2"-SW-200-061-A2-N
LV-2028 | Level control valve | LIC-2028 | D-201 hotwell water level | CFU-200-PR-PID-015 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 2"-SW-200-061-A2-N
LIC-2029 | Level indicating controller | LIC-2029 | D-201 slop oil level | CFU-200-PR-PID-015 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 2"-P-200-063-A1-N
LT-2029 | Level transmitter | LIC-2029 | D-201 slop oil level | CFU-200-PR-PID-015 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 2"-P-200-063-A1-N
LV-2029 | Level control valve | LIC-2029 | D-201 slop oil level | CFU-200-PR-PID-015 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 2"-P-200-063-A1-N
LIC-2030 | Level indicating controller | LIC-2030 | E-201 steam-generator level | CFU-200-PR-PID-014 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 2"-BFW-200-043-C1-H
LT-2030 | Level transmitter | LIC-2030 | E-201 steam-generator level | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 2"-BFW-200-043-C1-H
LV-2030 | Level control valve | LIC-2030 | E-201 steam-generator level | CFU-200-PR-PID-014 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 2"-BFW-200-043-C1-H
PIC-2031 | Pressure indicating controller | PIC-2031 | Vacuum off-gas to H-201 | CFU-200-PR-PID-015 | DCS | Soft (DCS function block) | 0-2.5 | barg |  |  |  | 2"-PG-200-023-A2-N
PT-2031 | Pressure transmitter | PIC-2031 | Vacuum off-gas to H-201 | CFU-200-PR-PID-015 | DCS | 4-20 mA HART | 0-2.5 | barg |  |  |  | 2"-PG-200-023-A2-N
PV-2031 | Pressure control valve | PIC-2031 | Vacuum off-gas to H-201 | CFU-200-PR-PID-015 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 2"-PG-200-023-A2-N
BY-2041 | Burner / flame BY | BY-2041 | Fire confirmation from F&G (P-204 area) | CFU-200-PR-PID-013 | F&G | DI 24 VDC |  |  |  | SIF-204 | SIL 1
EIV-2041 | Emergency isolation valve (ROSOV) | EIV-2041 | Pump P-112/P-204 hot-pump emergency isolation (fire) | CFU-200-PR-PID-013 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FC | SIF-204 | SIL 1
HS-2041 | Hand switch | HS-2041 | EIV-2041 manual close (CCR + field) | CFU-200-PR-PID-013 | SIS | DI 24 VDC |  |  |  | SIF-204 | SIL 1
TI-2100 | Temperature indicator | TI-2100 | H-201 pass 1 outlet temperature | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-600 | C |  |  |  | 12"-P-200-013-B3-H
TI-2101 | Temperature indicator | TI-2101 | H-201 pass 2 outlet temperature | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-600 | C |  |  |  | 12"-P-200-014-B3-H
TI-2102 | Temperature indicator | TI-2102 | H-201 pass 3 outlet temperature | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-600 | C |  |  |  | 12"-P-200-015-B3-H
TI-2103 | Temperature indicator | TI-2103 | H-201 pass 4 outlet temperature | CFU-200-PR-PID-012 | DCS | 4-20 mA HART | 0-600 | C |  |  |  | 12"-P-200-016-B3-H
PI-2104 | Pressure gauge | PI-2104 | Fuel gas supply pressure | CFU-200-PR-PID-012 | Local | - (local / mechanical) | 0-6 | barg |  |  |  | 4"-FG-200-019-A1-N
XV-2105 | On/off shutdown valve | XV-2105 | H-201 FG double block & bleed vent | CFU-200-PR-PID-012 | SIS | DO 24 VDC (SOV) + 2 x DI (ZSO/ZSC) |  |  | FO | SIF-201 | SIL 2
PCV-2106 | Self-acting pressure regulator | PCV-2106 | H-201 pilot gas self-acting regulator | CFU-200-PR-PID-012 | Local | - (local / mechanical)
TI-2107 | Temperature indicator | TI-2107 | C-201 flash zone temperature | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-600 | C |  |  |  | 54"-P-200-017-B3-H
PDI-2108 | Differential pressure indicator | PDI-2108 | C-201 dP top - flash zone | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-2.5 | bar
TI-2109 | Temperature indicator | TI-2109 | LVGO draw temperature | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-300 | C |  |  |  | 10"-P-200-025-B1-H
TI-2110 | Temperature indicator | TI-2110 | HVGO draw temperature | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 14"-P-200-027-B2-H
TI-2111 | Temperature indicator | TI-2111 | SLOP draw temperature | CFU-200-PR-PID-013 | DCS | 4-20 mA HART | 0-500 | C |  |  |  | 3"-P-200-030-B2-H
PI-2112 | Pressure gauge | PI-2112 | P-204A discharge pressure | CFU-200-PR-PID-013 | Local | - (local / mechanical) | 0-25 | barg |  |  |  | 6"-P-200-008-B2-ST
PI-2113 | Pressure gauge | PI-2113 | P-204B discharge pressure | CFU-200-PR-PID-013 | Local | - (local / mechanical) | 0-25 | barg |  |  |  | 6"-P-200-008-B2-ST
PI-2114 | Pressure gauge | PI-2114 | P-201A discharge pressure | CFU-200-PR-PID-014 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 6"-P-200-001-B1-H
PI-2115 | Pressure gauge | PI-2115 | P-201B discharge pressure | CFU-200-PR-PID-014 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 6"-P-200-001-B1-H
TI-2116 | Temperature indicator | TI-2116 | LVGO product temperature | CFU-200-PR-PID-014 | DCS | 4-20 mA HART | 0-120 | C |  |  |  | 4"-P-200-039-B1-N
PI-2117 | Pressure gauge | PI-2117 | P-202A discharge pressure | CFU-200-PR-PID-014 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 10"-P-200-005-B2-H
PI-2118 | Pressure gauge | PI-2118 | P-202B discharge pressure | CFU-200-PR-PID-014 | Local | - (local / mechanical) | 0-15 | barg |  |  |  | 10"-P-200-005-B2-H
PI-2119 | Pressure gauge | PI-2119 | P-203A discharge pressure | CFU-200-PR-PID-014 | Local | - (local / mechanical) | 0-12 | barg |  |  |  | 2"-P-200-031-B2-ST
PI-2120 | Pressure gauge | PI-2120 | P-203B discharge pressure | CFU-200-PR-PID-014 | Local | - (local / mechanical) | 0-12 | barg |  |  |  | 2"-P-200-031-B2-ST
TSV-2121 | Thermal safety valve | TSV-2121 | Thermal relief, CW sides E-115, E-202..E-204 (TSV-typ, D orifice, 3/4" x 1") | CFU-200-PR-PID-015 | Local | - (local / mechanical) | Set 7.0 | barg |  |  |  |  | TSV-typ
TI-2122 | Temperature indicator | TI-2122 | E-202 vapour outlet temperature | CFU-200-PR-PID-015 | DCS | 4-20 mA HART | 0-400 | C
TSV-2123 | Thermal safety valve | TSV-2123 | Thermal relief, CW sides E-115, E-202..E-204 (TSV-typ, D orifice, 3/4" x 1") | CFU-200-PR-PID-015 | Local | - (local / mechanical) | Set 7.0 | barg |  |  |  |  | TSV-typ
TI-2124 | Temperature indicator | TI-2124 | E-203 vapour outlet temperature | CFU-200-PR-PID-015 | DCS | 4-20 mA HART | 0-400 | C
TSV-2125 | Thermal safety valve | TSV-2125 | Thermal relief, CW sides E-115, E-202..E-204 (TSV-typ, D orifice, 3/4" x 1") | CFU-200-PR-PID-015 | Local | - (local / mechanical) | Set 7.0 | barg |  |  |  |  | TSV-typ
TI-2126 | Temperature indicator | TI-2126 | E-204 vapour outlet temperature | CFU-200-PR-PID-015 | DCS | 4-20 mA HART | 0-400 | C
PI-2127 | Pressure gauge | PI-2127 | P-205A discharge pressure | CFU-200-PR-PID-015 | Local | - (local / mechanical) | 0-8 | barg |  |  |  | 2"-SW-200-061-A2-N
PI-2128 | Pressure gauge | PI-2128 | P-205B discharge pressure | CFU-200-PR-PID-015 | Local | - (local / mechanical) | 0-8 | barg |  |  |  | 2"-SW-200-061-A2-N
PI-2129 | Pressure gauge | PI-2129 | P-206A discharge pressure | CFU-200-PR-PID-015 | Local | - (local / mechanical) | 0-8 | barg |  |  |  | 2"-P-200-063-A1-N
PI-2130 | Pressure gauge | PI-2130 | P-206B discharge pressure | CFU-200-PR-PID-015 | Local | - (local / mechanical) | 0-8 | barg |  |  |  | 2"-P-200-063-A1-N
HS-9000 | Hand switch | HS-9000 | Unit ESD push-button (CCR + field) | CFU-900-PR-PID-016 | SIS | DI 24 VDC |  |  |  | SIF-901 | SIL 2
UZ-9000 | Unit ESD logic (SIS) | UZ-9000 | Unit ESD-1 logic (SIS) | CFU-900-PR-PID-016 | SIS | 4-20 mA HART (SIS AI) |  |  |  | SIF-901 | SIL 2
PIC-9001 | Pressure indicating controller | PIC-9001 | Fuel gas header pressure | CFU-900-PR-PID-016 | DCS | Soft (DCS function block) | 0-6 | barg |  |  |  | 8"-FG-900-002-A1-N
PT-9001 | Pressure transmitter | PIC-9001 | Fuel gas header pressure | CFU-900-PR-PID-016 | DCS | 4-20 mA HART | 0-6 | barg |  |  |  | 8"-FG-900-002-A1-N
PV-9001 | Pressure control valve | PIC-9001 | Fuel gas header pressure | CFU-900-PR-PID-016 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 8"-FG-900-002-A1-N
LIC-9002 | Level indicating controller | LIC-9002 | D-103 liquid level | CFU-900-PR-PID-016 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 1"-BD-900-003-A1-N
LT-9002 | Level transmitter | LIC-9002 | D-103 liquid level | CFU-900-PR-PID-016 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 1"-BD-900-003-A1-N
LV-9002 | Level control valve | LIC-9002 | D-103 liquid level | CFU-900-PR-PID-016 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FC |  |  | 1"-BD-900-003-A1-N
LIC-9003 | Level indicating controller | LIC-9003 | D-104 flare KO drum level | CFU-900-PR-PID-016 | DCS | Soft (DCS function block) | 0-100 | % |  |  |  | 3"-BD-900-006-A1-N
LT-9003 | Level transmitter | LIC-9003 | D-104 flare KO drum level | CFU-900-PR-PID-016 | DCS | 4-20 mA HART | 0-100 | % |  |  |  | 3"-BD-900-006-A1-N
LY-9003 | Level relay / output | LIC-9003 | P-119A/B start/stop (high / low level) via MCC | CFU-900-PR-PID-016 | DCS | DO 24 VDC (interposing relay) | [5 empty] | 3"-BD-900-006-A1-N
PIC-9004 | Pressure indicating controller | PIC-9004 | LP steam header pressure (unit) | CFU-900-PR-PID-016 | DCS | Soft (DCS function block) | 0-6 | barg |  |  |  | 10"-LS-900-010-S1-H
PT-9004 | Pressure transmitter | PIC-9004 | LP steam header pressure (unit) | CFU-900-PR-PID-016 | DCS | 4-20 mA HART | 0-6 | barg |  |  |  | 10"-LS-900-010-S1-H
PV-9004 | Pressure control valve | PIC-9004 | LP steam header pressure (unit) | CFU-900-PR-PID-016 | DCS | 4-20 mA HART AO (smart positioner) |  |  | FO |  |  | 10"-LS-900-010-S1-H
PI-9100 | Pressure gauge | PI-9100 | P-119A discharge pressure | CFU-900-PR-PID-016 | Local | - (local / mechanical) | 0-10 | barg |  |  |  | 2"-BD-900-007-A1-N
PI-9101 | Pressure gauge | PI-9101 | P-119B discharge pressure | CFU-900-PR-PID-016 | Local | - (local / mechanical) | 0-10 | barg |  |  |  | 2"-BD-900-007-A1-N

## SIF List
SAFETY INSTRUMENTED FUNCTIONS
CFU-000-IC-IDX-001 Rev A - Issued for review (FEED) 2026-10-02 100 kBPSD CDU/VDU
SIF | Function | SIL | Initiators | Final elements | Instrument tags on P&IDs
SIF-101 | H-101 low-low pass flow (any pass) -> trip fuel | SIL 2 | FT-1011..1018 (2oo3 each pass) | XV-1021/1022 FG SSOV, XV-1026 pilot | FT-1011A, FT-1011B, FT-1011C, FT-1012A, FT-1012B, FT-1012C, FT-1013A, FT-1013B, FT-1013C, FT-1014A, FT-1014B, FT-1014C, FT-1015A, FT-1015B, FT-1015C, FT-1016A, FT-1016B, FT-1016C, FT-1017A, FT-1017B, FT-1017C, FT-1018A, FT-1018B, FT-1018C, FZLL-1011, FZLL-1012, FZLL-1013, FZLL-1014, FZLL-1015, FZLL-1016, FZLL-1017, FZLL-1018, XV-1021, XV-1022, XV-1026, XV-1230
SIF-102 | H-101 low-low fuel gas pressure -> trip fuel | SIL 1 | PT-1027A/B/C 2oo3 | XV-1021/1022 | PT-1027A, PT-1027B, PT-1027C, PZLL-1027
SIF-103 | H-101 high-high fuel gas pressure -> trip fuel | SIL 1 | PT-1027A/B/C 2oo3 | XV-1021/1022 | PZHH-1027
SIF-104 | H-101 loss of flame (all burners) -> trip fuel | SIL 2 | BS-1028 (scanners) | XV-1021/1022/1026 | BZLL-1028
SIF-105 | H-101 high-high arch pressure / loss of ID fan -> trip | SIL 1 | PT-1029A/B/C | XV-1021/1022 | PT-1029A, PT-1029B, PT-1029C, PZHH-1029
SIF-106 | H-101 high-high COT -> trip fuel | SIL 1 | TT-1020A/B/C 2oo3 | XV-1021/1022 | TT-1020A, TT-1020B, TT-1020C, TZHH-1020
SIF-107 | D-101A/B low-low interface (grid short) -> trip transformers | SIL 1 | LT-1007B / LT-1008B | Desalter transformer CB | LT-1007B, LT-1008B, LZLL-1007, LZLL-1008, XY-1007, XY-1008
SIF-108 | C-101 high-high bottom level -> stop P-101 / close FV-1001 | SIL 1 | LT-1082B | XV-1001 + P-101 trip | LT-1082B, LZHH-1082, XV-1001
SIF-109 | D-105 low-low level -> close LPG product XV (gas blow-by to LPG treating) | SIL 1 | LT-1092B | XV-1093 | LT-1092B, LZLL-1092, XV-1093
SIF-110 | C-105 high-high pressure -> cut reboiler steam | SIL 1 | PT-1091B | XV-1096 | PT-1091B, PZHH-1091, XV-1096
SIF-201 | H-201 low-low pass flow -> trip fuel | SIL 2 | FT-2001..2004 | XV-2006A/B | FT-2001A, FT-2001B, FT-2001C, FT-2002A, FT-2002B, FT-2002C, FT-2003A, FT-2003B, FT-2003C, FT-2004A, FT-2004B, FT-2004C, FZLL-2001, FZLL-2002, FZLL-2003, FZLL-2004, XV-2006A, XV-2006B, XV-2105
SIF-202 | H-201 low-low FG pressure / flame failure -> trip | SIL 1 | PT-2009A/B/C, BS-2008 | XV-2006A/B | BZLL-2008, PT-2009A, PT-2009B, PT-2009C, PZLL-2009
SIF-203 | C-201 high-high bottom level -> trip FV-1083 / P-112 | SIL 1 | LT-2024B | XV-1083 | LT-2024B, LZHH-2024, XV-1083
SIF-204 | Pump P-112/P-204 hot-pump emergency isolation (fire) | SIL 1 | Manual HS / fire detection | EIV-1121/EIV-2041 (ROSOV) | BY-1121, BY-2041, EIV-1121, EIV-2041, HS-1121, HS-2041
SIF-901 | Unit emergency shutdown (ESD-1, manual) | SIL 2 | HS-9000 (CCR + field) | All unit trip valves, heater trips | HS-9000, UZ-9000

## Summary
SUMMARY
CFU-000-IC-IDX-001 Rev A - Issued for review (FEED) 2026-10-02 100 kBPSD CDU/VDU
System | Count
DCS | 359
F&G | 4
Local | 128
SIS | 100
TOTAL | 591